## Slide 1
NACT 273
Industrial Boilers
Notes: First slide for 35mm show.

## Slide 2: House Keeping
Bathrooms
Emergency Evacuation
Cell Phones
Refreshments
Questions
Agenda

## Slide 3: Course Overview
Air Pollution
Boiler Uses
Boiler Theory and Operation
Air Pollution Formation
Air Pollution Control Devices
Boiler Regulations
Typical Permit Conditions
Inspection Procedures
Why
What
How

## Slide 4
NO2
NO
O
O2

## Slide 5: Uses of Boilers
Electrical generation
Space heating
Food preparation
Commercial laundries
Pulp & paper industry
Petroleum industry
Chemical industry
Municipalities : Water, Sewage & Garbage

## Slide 6: Uses of Boilers
Electrical generation
Space heating
Food preparation
Commercial laundries
Pulp & paper industry
Petroleum industry
Chemical industry
Municipalities : Water, Sewage & Garbage
High Pressure (2,000 -3,800 psi)
Low Pressure (150 – 1,600 psi)
Liquid water
Liquid water and steam
Saturated Steam
Superheated Steam

## Slide 7: Small Firetube Boiler

## Slide 8
Industrial Boiler

## Slide 9: Babcock & Wilcox Utility Boiler

## Slide 10
CO Catalyst
SCR Catalyst
HP Steam Drum
HP Boiler #1
HP Boiler #2
LP Boiler
Deaerator
LP Steam Drum / DA Storage
HRSG
Boiler

## Slide 11
Boilers &
Opacity

## Slide 12
History of Boilers : Ringelmann Chart

## Slide 13: Hot Numbers
British Thermal Unit (BTU)
  1 BTU the amount of energy needed to heat one pound of water one degree Fahrenheit or  energy given off by burning one wooden match
Lower Heating Value (LHV)
  Heating value of a fuel not counting
  heat needed to vaporize water
Higher Heating Value (HHV)
  Heating value of a fuel including heat needed to vaporize water

## Slide 14
Millions of BTU/hr
Boiler HP
Pounds of Steam/hr
Megawatts
Tons per day
Boiler Ratings

## Slide 15
Typical Boiler Rating

## Slide 16: Boiler Fuels
Natural gas
Diesel fuel oils
Tire Derived Fuel (TDF)
Coal/Petroleum Coke
Municipal waste
Bio-Mass
Waste gas
Nuclear

## Slide 17: Steam Plant Basic Elements

## Slide 18: Heat Transfer Methods
Notes: Radiant
Section

## Slide 19
Let’s Discuss Firetube &
Watertube Boilers

## Slide 20: Fire-Tube Boiler

## Slide 21: Fire-Tube Boiler

## Slide 22: Small Fire-Tube Boiler

## Slide 23
Fire-Tube Boiler

## Slide 24: Water-Tube Boiler

## Slide 25
Water-Tube Boiler

## Slide 26: Boiler Construction
Graphics Courtesy of ERI
Notes: The section of the boiler, where the primary method of heat transfer from the flame to the tubes is radiation :
is often called the furnace, firebox, or radiant section of the boiler
10,000 – 15,000 pph

## Slide 28
Boiler Tubes

## Slide 29
Boiler Tubes with Fins

## Slide 30
Boiler
Circulation

## Slide 31: Water to Steam Circulation Loop

## Slide 32
Boilers

## Slide 33
Natural
Circulation

## Slide 34
TEG Flow
Forced
Circulation

## Slide 35
Let’s Discuss Boiler
Air Requirements

## Slide 36: Boiler Air Requirements
Draft
  Natural
  Forced
  Induced
Combustion air
  Primary
  Secondary
  Excess

## Slide 37
Forced Draft Fans

## Slide 38
Induced Draft Fan

## Slide 39
Induced Draft Fans

## Slide 40: Gas Fired Water Tube Boiler

## Slide 41
Let’s Discuss Economizers
& Air-Preheaters

## Slide 42
Economizer – H2O Inside Tubes

## Slide 43
Air Pre-Heater

## Slide 44
Air Pre-Heater : Ambient to 400F +

## Slide 45
Fire Wall

## Slide 46
Refractory Lining
Boiler Tubes

## Slide 47
Boiler Tubes

## Slide 48
Let’s Discuss Fluidized
Bed Boilers

## Slide 49: Fluidized Bed Modes
Fixed
Bed
Minimum
Fluidization
Bubbling
Bed
Circulating
Bed
Start
No Air Flow

## Slide 50
Circulating Fluidized Bed (CFB)

## Slide 51
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 52
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater
1
2
3
4
5
6
7
8
9
10

## Slide 53: Fluidized Bed Distributor Plate & Bubble Caps
Graphic Courtesy of B&W

## Slide 54
Enclosed Conveyors
Feed Lot

## Slide 55
Fuel Storage Silo
Enclosed Conveyor

## Slide 56
Water to Steam Loop

## Slide 57
Furnace
Economizer
Air Preheater
Superheater

## Slide 58
Pulverized
Coal Lines:
Gravity Fed

## Slide 59
Inside the
Boiler

## Slide 60
Water Tubes

## Slide 61
Water
Tubes

## Slide 62
Re-cir.
Fines
Nozzle
????

## Slide 63
Distributor Plates & Bubble Caps

## Slide 64
Bubble
Caps

## Slide 65
Bed Nozzles & Underfire Air

## Slide 66
Ash
Loadout

## Slide 67
High Pressure Steam Drums

## Slide 68
Steam Drum w/Cyclone & Chevron Separators

## Slide 69: STEAM DRUM INTERNALS CYCLONES WITH MESH PAD
STEAM OUTLET
CONTINUOUS BLOWDOWN
FEEDWATER INLET
CHEMICAL FEED
FEEDERS
RISERS
VORTEX BREAKER
MESH PAD

## Slide 70: STEAM DRUM INTERNALS BAFFLE PLATE WITH MESH PAD
STEAM OUTLET
MESH PAD
RISER
BAFFLE
FEEDER
RISER
CONTINUOUS BLOWDOWN
CHEMICAL FEED

## Slide 71
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 72
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater
1
2
3
4
5
6
7
8
9
10

## Slide 73
Let’s Discuss
Power
Generation

## Slide 74
High Pressure Steam Lines

## Slide 75
High Pressure
Steam Lines

## Slide 76
Steam
Turbine

## Slide 77
Steam
Turbine

## Slide 78
Steam Turbine
Generator

## Slide 79
Cooling Towers

## Slide 80
Cooling Tower Shell

## Slide 81
Typical Control Room

## Slide 82
Utility Boiler
Steam
Turbine

## Slide 83
Steam
Turbine
Blades

## Slide 84
Steam Turbine

## Slide 85
HP Steam
Turbine

## Slide 86
Steam Turbine
Generator

## Slide 87: Brush DAX Turbogenerator

## Slide 88
Generator Rotor

## Slide 89
Generator Rotor

## Slide 90
Generator
Stator

## Slide 91
Step-Up Transformers

## Slide 92: Typical Electric Utility Plant
Boiler
Steam turbine
Generator
Cooling Media
Condenser
Deaerator
Stack
ESP
Induced Draft Fan
Forced Draft Fan
HP Feedwater Heaters
LP Feedwater Heaters
Fuel
Pump

## Slide 93
Lunch

## Slide 94
Let’s Discuss
Emissions
& Controls

## Slide 95: Emissions From Boilers
Fuel
+
Air
(N2, O2)
H2O
CO2
CO
NOX
HC
SOX
PM
CHO

## Slide 96: Emissions Control Methods
Boiler design
Proper maintenance
Operating conditions
Fuel types
Combustion
modifications
Exhaust treatment

## Slide 97: Control of Gaseous Emissions
Low-NOx burners
OFA
Ammonia injection (SNCR)
Catalysts (SCR)
FGR
FGD

## Slide 98: Combustion Considerations
Time
Temperature
Turbulence
Oxygen
Nitrogen

## Slide 99
 Thermal NOx
 Fuel-bound NOx
 Prompt NOx
NOx Creation

## Slide 100: Thermal NOx vs. Temperature
Graphic Courtesy of Coen

## Slide 101: COMBUSTION MODIFICATION
NOx FORMATION
  N + O NO
  N + OH NO + H
NOx REDUCTION
  CH + NO HCN + O2 (Reversible)
  CH2 + NO HCN + OH (Reversible)
  C + NO CN + O2
  NHi + NO N2 + H2O
  THESE NOx REDUCTANTS ARE FORMED BY PARTIAL COMBUSTION IN A REDUCING ATMOSPHERE
  THE INTERMEDIATE SPECIES, HCN & CN, ARE CONVERTED TO N2, CO2 & H2O IN THE FINAL BURNOUT ZONE

## Slide 102: PROMPT NOx
Rapid Formation <1ms.
Little affect from temperature.
Presence of CHi & HCN during initial combustion can contribute to prompt NOx formation in an oxidizing environment, but will inhibit NOx formation in a reducing environment.
Presence of C & NHi in initial combustion process reduces the formation of prompt NOx.
Reactor combustion is controlled to a stoichiometry <.6 and a temperature <2400F.

## Slide 103: PROMPT NOx
N2
HCN
+C
CN
NO
+O
NCO
NHi
+CH2
+H
+OH
+H20
HNCO
+NO
+CH3
H2CN
+NHi
NO2
O2, H2O
HOCN
H

## Slide 104: NOx Production vs. Air/Fuel Ratio
Graphic Courtesy of Coen

## Slide 105: Industry Burner Definitions
Modern conventional burners
  NOx less than 80 ppm (<0.1 lb/MMBtu)
Low-NOx burners
  NOx less than 30 ppm
  (<0.04 lb/MMBtu)
Ultra Low-NOx burners
  9 ppm NOx
  (<0.01 lb/MMBtu)

## Slide 106
Let’s Discuss FGR

## Slide 107: Flue Gas Recirculation (FGR)

## Slide 108: Flue Gas Recirculation (FGR)

## Slide 109: Flue Gas Recirculation (FGR)

## Slide 110
FGR : Flue Gas
Recirculation

## Slide 111: FGR BURNERS
FEATURES
CAN USE FGR FLOWS AS HIGH AS 40% OF THE TOTAL STACK EFFLUENT
SOME SYSTEMS OPERATE VERY CLOSE TO THE LIMITS OF FLAMABILITY
SOME SYSTEMS OPERATE WITH VERY RAPID MIXING, VERY CLOSE TO STOICHIOMETERY.
CON’S
HIGH ELECTRICAL USAGE (FGR fan HP doubled compared to RX system)
LOW TEMPERATURE, TRANSLUCENT, FLAME REDUCES HEAT TRANSFER & EFFICIENCY.
COMBUSTION INSTABILITY
CAN’T CHANGE FIRING RATE FAST ENOUGH TO FOLLOW CHANGING LOAD DEMANDS

## Slide 112: Lower Cost to Industry
Simple durable refractory and steel construction results in:
  Lower initial cost
  Lower maintenance costs
Lower operating cost
  Less stack losses due to low excess air and low FGR requirements
  Lower fan costs
  Eliminates the need for chemicals & catalysts

## Slide 113: Flame Temperature vs. FGR
Graphic Courtesy of Coen

## Slide 114: FGR Impact

## Slide 115
Let’s Discuss
Staged Combustion

## Slide 116: Gas Pre-mix Burner

## Slide 117: Low-NOx Burner with Staged Fuel

## Slide 118: Low-NOx Burner with Staged Fuel
Notes: TQ
#12
TQ
#11

## Slide 119
Ultra Low-NOx Burner (9 ppm)

## Slide 122: Burner Cross-sectional View

## Slide 123: TYPICAL COMPONENTS
Fuel valves & Servos
Lean Jet
Reactor

## Slide 124: TYPICAL COMPONENTS
REACTOR PORT
LEAN JETS

## Slide 125: A Look Down the Furnace
Rich Flame
Lean Flames (x4)
Burnout Zone
FGR

## Slide 126: Staged Combustion with Overfire Air

## Slide 127: Burners with Overfire Air
Graphic Courtesy of B&W

## Slide 128: NOx Reduction by Boiler Configuration
A B C
A: Low-NOx burner only, no overfire air (OFA)
B: Low-NOx burner with OFA
C: Low-NOx burner with OFA and FGR
Graphic Courtesy of B&W

## Slide 129: COST $/ TON NOx REMOVED NEW BOILER SYSTEMS
POST COMBUSTION
$ 24500 (SCR)
MASSIVE FGR
  $ 3676
POROUS MATRIX
$ 2787
ULTRA LOW NOX TECHNOLOGY
$258

## Slide 130: Existing Emissions & Goals
Emission | Existing | Proposed
NOx ppm@3% O2 | 25.3 | 5 - 6
CO ppm@ 3% O2 | 70.2 | <50
Stack O2, % | 6.2 | 2.5 – 3.2
Reduce NOx by 75%
Reduce O2 by 48 - 60%
Reducing O2 from 6% to 3% saves this customer 273 CFH of nat gas

## Slide 131
Let’s Discuss
SCR
Catalyst

## Slide 132: Selective Catalytic Reduction (SCR)
NOx control thru ammonia (NH3) injection
4NO + 4NH3 + O2  4N2 + 6H2O
2NO2 + 4NH3 + O2  3N2 + 6H2O
90-95% control
Problems
  Expensive
  High maintenance
  Ammonia “slip”
  Catalyst replacement & disposal

## Slide 133
Small Boiler with SCR

## Slide 134: Boiler with Retrofit SCR

## Slide 135
Ammonia Storage Tank

## Slide 136
Anhydrous Ammonia Storage Tank

## Slide 137
Utility Boiler NH3 Manifold

## Slide 138
NH3 Injection Tube

## Slide 139
SCR Catalyst

## Slide 140: % NOx Removed vs. Vanadium Pentoxide Catalyst Temperature

## Slide 141
Boilers
& SNCR

## Slide 142: Boiler With SNCR

## Slide 143: Selective Non-Catalytic Reduction
NOx control through ammonia or urea injection
No catalyst necessary
Temperature range 1400 oF – 1700 oF
Injected upstream of convection section
80% control under normal conditions
Problems:
  Changing flue temperatures with changing load
  Formation of ammonium salts
  Ammonia slip
Catalyst

## Slide 144: Comparison of NOx Reduction Technologies
Technology | Approx. Reduction | Approx. lbs/MMBTU | Approx. ppmv @ 3% O2
Standard burners | Base case | 0.14 | 120
Low NOx burners | 60% | 0.06 | 45
Ultra Low NOx burners – Ist gen. | 80% | 0.03 | 25 - 30
Ultra Low NOx burners – 2nd gen. | 95% | 0.007 | 6 - 9
FGR | 55% | 0.025 | 20
Compu- NOx w/ FGR | 90% | 0.015 | 15 - 20
SNCR | 80% | 0.033 - 0.085 | 27 - 70
Catalytic Scrubbing | 70% | 0.017 - 0.044 | 14 - 36
SCR | 90 – 95% | 0.006 - 0.015 | 5 - 12

## Slide 145
Let’s Discuss
SOx Control

## Slide 146: Fuel Sulfur Content
Sulfur Content of Various Fuels
Fuel
Sulfur
Percent by Weight
Natural gas
0.0005
LPG
0.001
Fuel Oil No. 1
0.01 to 0.3
Fuel Oil No. 2
0.05 to 0.5
Diesel Motor Fuel
0.0015
Fuel Oil No. 4
0.2 to 1.75
Fuel Oil No. 5
0.5 to 1.75
Fuel Oil No. 6
0.5 to 1.75
Low Sulfur
Fuel Oil No. 6
0.5
Subbituminous coal
from Rocky Mt. states
0.3 to 1
Petroleum coke
2 to 10
Notes: TQ
#15

## Slide 147: Spray Tower Wet FGD Scrubber
Graphic Courtesy of B&W

## Slide 148: Five FGD Scrubber Modules on Utility Boiler
Graphic Courtesy of B&W

## Slide 149
Let’s Discuss
PM Control

## Slide 150: Control of Particulate Emissions
Settling chambers
Cyclones
Baghouses
ESPs
Scrubbers

## Slide 151
Water Spray

## Slide 152
Soot Blowing

## Slide 153
Soot Blowers

## Slide 154
Soot Blowing/ Rapping

## Slide 155
Cyclone

## Slide 156: Multi-Cyclone
Graphic Courtesy of B&W

## Slide 157
Baghouse

## Slide 158
Baghouse
Clean
Dirty

## Slide 159
ESP

## Slide 160
Regulatory
Requirements

## Slide 161: Regulatory Requirements
Federal, state, and local requirements
Boiler specific limits
Permit requirements
Monitoring requirements
Visible emission limits
Nuisance regulations
Breakdowns & variances

## Slide 162: Boiler Regulations
NSPS 40 CFR Part 60 Subpart D, Da, Db, Dc, Ea
Acid Rain Provisions (Parts 72,73,74,75, 76, 77, 78)
RCRA 40 CFR Parts 264 & 266
State Regulations including VE
SIP Requirements
Local Regulations
MACTs – JJJJJJ & DDDDD
Notes: USEPA regulations place limits on boiler emissions in NSPS & NESHAPS & ACID RAIN regulations.
Title 40 Part 60 Subparts D, Da, Db, and Dc of the CFR place emission limits on some steam generation units built since 1971.
Title 40 Part 63 Subparts JJJJJJ & DDDDD place emission limits toxic air contaminants
PM as surrogate for Heavy Metals
Hg
HCl as surrogate for inorganic HAPs
CO as surrogate for organic HAPS
based primarily on size, design and fuels used in boilers.

## Slide 163: Boiler Emission Limits
NOx, SO2, particulate, and opacity values for boilers are based on applicable subpart, heat input, date built or modified, and fuel used
States and districts may have more stringent limits

## Slide 164
BACT in CA

## Slide 165
BARCT & RACT

## Slide 166: Permit Categories
Emissions Limitations
Equipment Requirements
Operating Conditions
Monitoring and Recording Requirements
Compliance Testing
General Requirements

## Slide 167: Testing and Monitoring
Continuous Monitoring System
Stack Testing
Process Monitors
Recordkeeping

## Slide 168: Continuous Monitoring Types
Opacity Transmissometers
NOX
SO2
CO
O2 and/or CO2
Ammonia
Mercury Semi-Continuous

## Slide 169: Source Testing
Particulate Matter (PM, PM10, PM2.5)
NOx, SO2, CO, Ammonia
Mercury and Other Metals
Hydrogen Chloride
Formaldehyde
Visible Emissions (Method 9)

## Slide 170: Control Device Parameters
ESP Spark Rate and Fields in service
Baghouse Pressure Drop
Scrubber Pressure Drop and Liquor Flow Rate
Fuel Usage

## Slide 171: Alternative Monitoring
Portable analyzer monitoring of NOx, CO, O2
Determination of FGR rate
Burner mechanical adjustments
O2 Trim concentration
FGR valve(s) setting
Portable Combustion Analyzer

## Slide 172
Boiler Inspections

## Slide 173
 Capture
 Transport
 Air mover
 Control device
 Instrumentation
 Subsystem
 Records
Points of
Inspection

## Slide 174: Pre-Inspection
Prepare inspection form
File review
Regulation review
Equipment check
Pre-entry & entry
Pre-inspection meeting
Permit check

## Slide 175: Reasons for Inspections
Compliance determination
Complaint investigation
Source plan approval
Review or renewal of permits
Special studies
AQMD

## Slide 176: Inspection
Visible emission evaluation
General upkeep & maintenance
Monitoring instruments & records
Fuel type and quality
Maintenance records
Operational records
Source tests

## Slide 177
Plant
Safety

## Slide 178: Inspector Safety
Proper equipment
Plant warnings
Heat
High pressure steam
Electrical hazards
Noise
Moving parts
Inhalation hazards
Hazardous materials
Machine disintegration
Fires
Other hazards & traps
Notes: TQ
#24

## Slide 179
Plant Safety

## Slide 180
Plant Hazards

## Slide 181
Confined
Space

## Slide 182
Confined
Space

## Slide 184
HP Gas Lines

## Slide 185
Ruptured
Steam Line

## Slide 186
Steam
Exhaust

## Slide 187
Access

## Slide 188
Access

## Slide 189
Thank You!