MODULE 3: PERFORMANCE SPECIFICATIONS, QUALITY ASSURANCE, AND COMMONLY USED TECHNOLOGIES

# Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies

Module 3 Description:

In Module 3, participants will be provided an overview of performance specifications (PS) used for evaluating the acceptability of continuous monitoring systems (CMS) at the time of, or soon after, installation and wherever specified in the regulation. They will also learn about the associated quality assurance (QA) procedures, detailed information about each PS, and commonly used technologies.

Module 3 Learning Objectives:

- Define key terms, such as calibration drift (CD), relative accuracy (RA), span value, etc.

- Compare performance specification (PS) and quality assurance (QA) procedures by pollutant, where relevant

- List relevant QA procedures by PS

- Provide examples of technologies that can be used for each PS

- Recognize why predictive emission monitoring systems (PEMS) PS are different from others

Module 3 Preparation:

- Flip-chart page for each small group for optional culminating activity

Estimated Time: 525 minutes (8.75 hours)

| Slide 1 Optional Opening Exercises: Before beginning Module 3, give participants an opportunity to review the learning from the previous day by conducting one of the following opening exercises: - Participants write for five minutes about the previous day’s topic. On a flip chart, record any questions that arise. Then, discuss as a class. - Participants write down on a sticky note one thing they learned yesterday that was useful or helpful to their job. Post these sticky notes on a wall/flip chart for other participants to view. Discuss these learning moments as a class. | Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies Instructor Notes: - Introduce Module 3. SAY: “Module 3 is intended as an overview of performance specifications and their associated QA procedures and commonly used technologies. Let’s look more closely at the topics this module will cover.” |
| --- | --- |

| Slide 2 | Module 3 Outline Instructor Notes: - Review the topics covered in the Module 3 outline. - Explain to participants that they will first be provided with commonly used terms and definitions. DIRECT: - Direct participants to the CMS Definitions by PS handout for definitions specific to each performance specification (PS). - Explain that, where applicable, this module covers commonly used technologies. These are intended as examples only and are not prescriptive or comprehensive. Direct participants to the Commonly Used Technologies handout. - Tell participants that PS-2 includes elements that are common to many of the other performance specifications. As a result, this module does not repeat features of PS-2, but rather, covers only those elements that are unique to the respective PS. DIRECT: - Direct participants to the Commonly Used Acronyms handout for Module 3. - Explain to participants that they may find this helpful to refer to during the module. |
| --- | --- |

| Slide 3 | Module 3 Learning Objectives Instructor Notes: SAY: “Here are the objectives that you should be able to accomplish after we complete this module.” Read the Module 3 learning objectives. |
| --- | --- |

| Slide 4 | Introduction to Performance Specifications Instructor Notes: - Explain what will be covered in this module. SAY: “This module will provide an overview of performance specifications that are published in the Code of Federal Regulations or CFR, and for those that are pollutant-specific, this module will cover the associated commonly used technologies and QA procedures.” - Tell participants that elements such as the reference test methods that are to be used for continuous emission monitoring systems (CEMS) certification testing, are usually specified in the applicable performance specification. |
| --- | --- |

| Slide 5 | Introduction to Performance Specifications (Cont’d) Instructor Notes: - Discuss the additional information on the slide about performance specifications. |
| --- | --- |

| Slide 6 | Introduction to Quality Control and Quality Assurance Instructor Notes: - Define quality control (QC) and quality assurance (QA). - Explain the difference between QC and QA and how it relates to performance specifications. - Point out that QC procedures are routine activities. These activities include, but are not limited to, daily calibrations, quarterly CGAs, annual RATAs and routine preventive maintenance activities as defined by manufacturers of the various hardware components of CEMS and/or by regulatory agencies. |
| --- | --- |

| Slide 7 | Technology Neutral Instructor Notes: - Explain the term “technology neutral” in relation to PS and QA procedures. DIRECT: - Direct participants to the Performance Testing handout for definitions specific to each PS. |
| --- | --- |

| Slide 8 | To Be Covered…. Instructor Notes: - Explain what PS will be covered in this module. Tell participants that this is a list of all PS and QA procedures that have been promulgated or finalized. There are a few other PS that were proposed, but never finalized. DIRECT: - Direct participants to the Performance Specifications handout. - Give participants a few minutes to familiarize themselves with the contents of the handout and how it is organized. - Explain that it will match up with the presentations for today. Point out that the handout is organized in chronological order showing performance specifications and QA procedures. SAY: “As you can see, your performance specifications are generally organized by pollutant or a specific technology and there are procedures that can be shared across the performance specifications.” SAY: “In the next couple of days we will review the 18 PS, along with their associated pollutants and QA procedures, as listed in this table.” |
| --- | --- |

| Slide 9 | Setting the Stage: Commonly Used Terms Instructor Notes: - Review the seven commonly used terms on the next two slides. - Tell participants that these commonly used terms are located in the Master Glossary for this course. - Tell participants it is important to note that many of these definitions pertain to PS-2, but for any definition that differs, we will review in the course today and include in the CMS Definitions by Performance Specification (PS) handout. |
| --- | --- |

| Slide 10 | Setting the Stage: Calibration Error and Calibration Drift Instructor Notes: - Continue to review commonly used terms. |
| --- | --- |

| Slide 11 | Setting the Stage: Response Time and Out-of-Control Instructor Notes: - Continue to review commonly used terms. |
| --- | --- |

| Slide 12 | Quality Assurance Procedure Audits Instructor Notes: - Explain why QA procedure audits are critical. - Review the four main types of audits discussed in QA procedures. |
| --- | --- |

| Slide 13 | What is a Relative Accuracy Test Audit? Instructor Notes: - Define relative accuracy test audit (RATA). - Discuss details on how a RATA is performed: - After completion, the 9 runs of reference method (RM) test data are compared to the continuous monitoring systems (CMS) data from the same time periods. Then, the relative accuracy (RA) is calculated. - The equations used to calculate the RA, along with the acceptability criteria for the RATA, can be found in the performance specifications and QA procedures. - The RATA is the only test that confirms that the sampling probe is providing a representative stack gas sample. |
| --- | --- |

| Slide 14 NOTE: Each audit gas is injected non-sequentially into the CEMS multiple times. The gas must pass through the whole sampling system. The CEMS readings of the audit gases are recorded. The equations used to determine the acceptability of the CGA are found in the PS and QA procedures. | What is a Cylinder Gas Audit? Instructor Notes: - Define cylinder gas audit (CGA). |
| --- | --- |
| Slide 15 | What is a Calibration Drift Assessment? Instructor Notes: - Define calibration drift (CD) assessment. - Explain the following information about a calibration drift assessment: - Two calibration gases, a zero- and higher-level, are injected into the CEMS approximately every 24-hours. - The PS and QA procedure specify the required range of the calibration gases. - The equations used to calculate the CD and the CD acceptability criteria are found in the PS and QA procedures. - Acceptance criteria for an initial 7-day drift test and daily drift test are usually different. A 7-day drift has a tighter acceptance criteria. |

| Slide 16 NOTE: The equations used to calculate RA, along with the acceptability criteria, can be found in the PS and QA procedures. | What is a Relative Accuracy Audit? Instructor Notes: - Define relative accuracy audit (RAA). |
| --- | --- |

| Slide 17 | Performance Specification 1 (PS-1) Instructor Notes: SAY: “Now, let’s discuss PS-1, which includes specifications and test procedures for continuous opacity monitoring systems (COMS) in stationary sources.” |
| --- | --- |

| Slide 18 | PS-1 Requirements Instructor Notes: - Highlight the requirements under PS-1. - Tell participants these requirements will be discussed in more detail on the following slides. |
| --- | --- |

| Slide 19 | Requirements for Manufacturers Instructor Notes: - Explain what opacity manufacturers must comply with. - Discuss the following requirements for manufacturers: - Conduct the verification procedures for design specifications in Section 6 of ASTM D 6216- 12. - Conduct the verification procedures for performance specifications in Section 7 of ASTM D 6216-12. - Provide to the owner or operator, a report of the opacity monitor's conformance to the design and performance specifications required in Sections 6 and 7 of ASTM D 6216-12 in accordance with the reporting requirements of Section 9 in ASTM D 6216-12. |
| --- | --- |

| Slide 20 | Requirements for Owners/Operators: Installation Instructor Notes: - Explain the installation requirements for owners/operators. IMPORTANT/KEY MESSAGE: - Highlight that installed COMS must be accessible for maintenance. |
| --- | --- |

| Slide 21 NOTE: Optical alignment is an indication of alignment that is objectively apparent relative to reference markers or conditions. | Requirements for Owners/Operators: Performance Tests Instructor Notes: - Explain the requirements for owners/operators when conducting a calibration error (CE) check and optical alignment assessment. - Explain that a three-point CE check is conducted using three calibration attenuators as specified by ASTM D 6216-12: - The attenuator must be in place for at least two times the shortest recording interval on the COMS data recorder. - The three-point CE check must capture five non-consecutive readings for each attenuator. - If the COMS only records 6-minute averages, then the attenuator must remain in place for at least 12 minutes in order to ensure that a 6-minute average is recorded by the data acquisition system. - Define optical alignment. |
| --- | --- |

| Slide 22 | Requirements for Owners/Operators: Performance Tests (Cont’d) Instructor Notes: - Explain the requirements for owners/operators when conducting a calibration error (CE) check and optical alignment assessment. |
| --- | --- |

| Slide 23 | Operational Test Period Instructor Notes: - Describe operational test period parameters. - Explain that during a shut-down, the clock stops, so there are no measurements. In total, 168 hours of normal operation are required. |
| --- | --- |

| Slide 24 NOTE: Sources that achieve quality assured data for four consecutive quarters may reduce their auditing frequency to semi-annual. If a performance audit is failed, the source must resume quarterly testing for that audit requirement until it again demonstrates successful performance over four consecutive quarters. | Procedure 3 – Quality Assurance Requirements for Continuous Opacity Monitoring Systems at Stationary Sources Instructor Notes: - Review the basic functions and requirements of Procedure 3. |
| --- | --- |

| Slide 25 | Procedure 3 - Limitations Instructor Notes: - Review the limitations of Procedure 3. - Explain that COMS must be located where condensed water vapor is not present. |
| --- | --- |

| Slide 26 NOTE: A program of corrective action for a malfunctioning COMS must include, at a minimum, the requirements specified in Section 10.5 of Procedure 3. | Procedure 3 – Required Quality Control Program Instructor Notes: - Explain the QC program as it relates to Procedure 3. - For procedures for performing drift checks, tell participants that these must include both zero and upscale drift and the status indicators check. |
| --- | --- |

| Slide 27 | Procedure 3 – Auditing Requirements Instructor Notes: - Explain auditing requirements for Procedure 3. - Tell participants these important points about auditing requirements: - Evaluate what corrective action must be taken whenever the daily zero drift exceeds twice the applicable drift specification in Section 13.3(6) of PS-1. - Take appropriate corrective action based on the manufacturer's recommendations when the COMS is operating outside preset limits. - Conduct a 3-point calibration error test. The low, mid-, and high-range calibration error results must be computed as the mean difference and 95% confidence interval for the difference between the expected and actual responses of the monitor as corrected to stack exit conditions. - Describe the quarterly auditing requirements for COMS according to section 10.2. |
| --- | --- |

| Slide 28 | Procedure 3 – Limits for Excessive Inaccuracy Instructor Notes: - Discuss allowable audit inaccuracy for Procedure 3. |
| --- | --- |

| Slide 29 | Procedure 3 – Corrective Actions Instructor Notes: - Discuss corrective actions for Procedure 3. |
| --- | --- |

| Slide 30 | Opacity Transceiver Instructor Notes: - Tell participants that transceivers and retroreflectors both include: - Air purging or blower systems which keep the optical windows clean - Protective shutters that close to protect the optics if the blower system quits |
| --- | --- |

| Slide 31 | Commonly Used Technology - Transmissometry Instructor Notes: - Define transmissometry. |
| --- | --- |

| Slide 32 | Double Pass Transmissometer Instructor Notes: - Describe the double pass transmissiometer: - There is a light source and detector all in one unit (transceiver) on one side of the stack and a light beam reflector (retroreflector) on the other. - Modern light sources contain a light-emitting diode (LED). - By reflecting the projected light from a mirror on the opposite side of the stack: - Double-pass systems can be easily designed to isolate and check the electronic circuitry in the system all on one side of the stack. - The double pass design allows for twice the light path of a single-pass system which increases the sensitivity and accuracy of the monitor. - Alignment criteria (design and QA) ensures no loss of light by misalignment of a transmissometer and retroreflector. - Most systems have blowers on both a transmissometer and retroreflector to keep optical windows clean. |
| --- | --- |

| Slide 33 | Double Pass Transmissometer (Cont’d) Instructor Notes: SAY: “We’ll now discuss the components of the double pass transmissometer.” - Discuss the main components of the double pass transmissometer: - Light source: Typically an LED - Modulator: Rotates through a light path to cause a pulsed or modulated light; the detector and electronics are designed to only monitor the pulsed light and be unaffected by any ambient light leakage. - Reflective chopper: Allows light to pass through to a retroreflector or to be reflected back to the detector to get a reference value for the light. - Beam splitter: A half-silvered mirror that can reflect and transmit a light beam; it allows a light beam to pass through it to the rotating chopper. It also allows a returning beam from across the stack to be reflected down to the detector. - Calibration system: A zero-reflector mirror for zero % opacity and a higher value span opacity slide that can be inserted into the light path. - Explain the operation of the double pass transmissometer: - The chopper bounces the beam back to the beam splitter which reflects light down to the detector *(IO - Reference Zero Value) - Light makes double pass: *(I - Light Intensity measured after it passes through flue gas) *I/ IO = Fractional Transmittance |
| --- | --- |
| Slide 34 OPTIONAL KNOWELDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 1. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s participate in a game to test your knowledge of the information you’ve learned so far.” ACTIVITY - Divide class into groups with 3 or 4 participants per group. - Use the flipchart to capture team names and points. - Explain the directions to the participants: - The instructor will read the first knowledge check on the screen. Groups will quietly discuss their answer and raise their hand when they have an answer. - The instructor will call on the first group who raise their hands. - The instructor will record a point for each group/team that answers correctly. This game format continues for all the knowledge check questions. - Tell participants that this game will continue until the end of Module 3 since there are additional questions to come. Explain that those groups/teams who get the most points will receive a reward (e.g., extra break tomorrow). Proceed to the following slides to conduct the activity. |

| Slide 35 | PS-1 and Procedure 3 Instructor Notes: - What are the requirements of the CD test under PS-1? Answer: Procedures for performing drift checks must include both zero and upscale drift and the status indicators check. - How is system response time determined? Answer: System response time is determined by measuring the amount of time needed for a 95% step change in the COMS data recorder. - What is the OOC period for each audit in procedure 3? Answer: - Daily Audit - if the zero drift check or upscale drift check exceeds twice the applicable drift specification in PS-1 for any one day - Quarterly audit - if: - The optical alignment indicator does not show proper alignment, - The zero compensation exceeds 4% opacity, or - The CE exceeds 3% opacity - Annual audit - if the zero-alignment error exceeds 2% opacity. - What are the responsibilities of the opacity monitor manufacturer? Answer: Opacity manufacturers must comply with a comprehensive series of design and performance specifications and test procedures to certify opacity monitoring equipment before shipment to the end user. |
| --- | --- |

| Slide 36 | Performance Specification 2 (PS-2) Instructor Notes: SAY: “Now, let’s discuss PS-2, which includes specifications and test procedures for sulfur dioxide and oxides of nitrogen in stationary sources.” |
| --- | --- |

| Slide 37 NOTE: PS-2 serves as the framework for most other performance specifications. | Overview of PS-2 Instructor Notes: - Provide an overview of PS-2. - PS-2 is for evaluating the acceptability of SO2 and NOX CEMS at the time of installation or soon after and whenever specified in the regulations. The CEMS may include, for certain stationary sources, a diluent (O2 or CO2) monitor. - PS-2 includes installation and measurement specifications, as well as calibrations and audit requirements for: - CD test - RATA |
| --- | --- |

| Slide 38 | CEMS Installation and Measurement Location Specifications Instructor Notes: - Explain CEMS installation and measurement location specifications: - Must be in an accessible location that is representative of the emissions from the unit - At least 2 equivalent diameters downstream from nearest control device and at least ½ equivalent diameter upstream from the effluent exhaust SAY: “Those of you familiar with Reference Method 1 in 40 CFR 60, Appendix A will recognize those values.” - Discuss measurements for point CEMS and path CEMS: - Point CEMS - no less than 1 meter from stack wall / within or centrally located over any part of the centroid area of the stack or duct cross section - Path CEMS – effective measurement path totally within the inner area bounded by a line 1 meter from the stack or duct wall, or has at least 70% of the path within the inner 50% of the stack or duct cross-sectional area, or be centrally located over any part of the centroidal area |
| --- | --- |

| Slide 39 | Calibration Drift Test Instructor Notes: - Explain the CD test. - Test period includes determining the magnitude of CD once each day at 24-hr intervals - If the CEMS includes pollutant and diluent monitors, the CD must be determined separately for each in terms of concentrations, and none of the CDs may exceed the specification. - Example data sheet for CD test provided as Figure 2-1 of PS-2. IMPORTANT/KEY MESSAGE: If periodic automatic or manual adjustments are made to the CEMS zero and calibration settings, conduct the CD test immediately before these adjustments. |
| --- | --- |

| Slide 40 NOTE: Stratified means that the emissions are not evenly distributed across the stack or duct | Relative Accuracy Test Audit Instructor Notes: - Describe relative accuracy test audit: - RATA determines the absolute mean difference between the gas concentration or emission rate determined by the CEMS and the value determined by the RM, plus the 2.5 % error confidence coefficient of a series of tests, divided by the mean of the RM tests or the applicable emission limit. - Explain that the RATA is the only test that tells us if the sampling probe was located at a representative spot in the emissions stream. |
| --- | --- |
| Slide 41 NOTE: Stratification is generally defined as a difference in excess of 10% between the average concentration at any point more than 1 meter from the duct or stack wall. | Determining if Stratification Exists Instructor Notes: - Explain how to determine existence of stratification. - Explain that this slide illustrates velocity isopleths in a rectangular stack. - This image shows variation looking down the stack. The dots are traverse points, the numbers represent the velocity. - Remind students what traverse points are. - Provide the following information about stratification: - If stratification exists, the 16.7, 50 83.3 traverse points must be used - The principle of Method 1 rests on the assumption that if testing is done at a point that is close to a bend in the ductwork, close to a fan, or close to some other disturbance such as stack exit, the flow will not be uniform. - The assumption is that flue gas velocity and/or particulate matter concentration will be more stratified the closer we get to flow disturbance. |

| Slide 42 | Reference Method Traverse Points Minimum Requirements Instructor Notes: - Describe the minimum requirements for reference method traverse points: - Measurement Line – through the centroidal area and in the direction of any expected stratification - If this interferes with the CEMS measurements, displace the line up to 30 cm (12 inches) or 5% of the equivalent diameter of the cross section (whichever is less) from the centroidal area. - The measurement line should include 3 traverse points: 16.7, 50.0 and 83.3% of the duct/stack diameter (this is often referred to as a “3-point long line”). - If the measurement line is > 2.4 m (7.8 ft) and no stratification expected, then use 0.4, 1.2 and 2m from stack/duct wall for the traverse points (this is often referred to as a “3-point short line”). - Explain that this option cannot be used with a wet scrubber or at points where two streams with different pollutant concentrations combine. |
| --- | --- |

| Slide 43 NOTE: More than nine sets of RM tests may be performed. A maximum of three test runs may be rejected as long as the total number of test results used to determine the RA is greater than or equal to nine. For three traverse points on the measurement line, use 7 minutes at each traverse point (21 minutes total). Integrated Samples: - Minimum of 21 minutes sampling strategy - Equal time at each traverse point Grab Samples (if using Method 6 or Method 7): - One sample at each traverse point Three samples per run taken simultaneously or at an equal interval of time apart across the time the CEM pollutant is measured (at least three separate measurements). | Relative Accuracy Test Audit Procedure Instructor Notes: - Explain the RATA procedure. - Discuss the following information about the RATA: - When performing a RATA, select an appropriate sampling location at least two equivalent diameters downstream of any flow disturbance or other point at which a change in the pollutant concentration or emission rate may occur, and at least a half equivalent diameter upstream from the effluent exhaust or control device. - Conduct the RATA according to the procedure given while the affected facility is operating at more than 50% of normal load, or as specified in an applicable subpart. The RATA may be conducted during the CD test period. - Unless otherwise specified in an applicable subpart of the regulations, the following test methods, or their approved alternatives, are the required reference methods: - Method 3B – O2 and CO2 - Method 4 – moisture in stack gas - Method 6 – SO2 - Method 7 – NOx Note: while the above methods are required through PS-2, there are other methods that can be used as well. |
| --- | --- |

| Slide 44 | Relative Accuracy Performance Criteria Instructor Notes: - Explain the RA PS. - Provide the following information about RA PS: - Diluent specifications are in PS-3 and cannot be exceeded - RA: Only use the 10% criteria when emissions are less than 50% of your allowable - SO2 has additional options: 15% of the applicable standard if emissions are between .30 and .20 lb/mBtu. If less than .20, 20% of the applicable standard can be used IMPORTANT/KEY MESSAGE: PS-2 has different requirements based on the level of SO2 emissions (different from everywhere else). - Point out the criteria that apply in each situation. |
| --- | --- |

| Slide 45 | Procedure 1 – Quality Assurance Requirements for Gas CEMS Used for Compliance Determination Instructor Notes: - Explain the procedure for QA requirements for gas CEMS used for compliance determination: - This procedure treats QC requirements in general terms to allow each source owner or operator to develop a QC system that is most effective and efficient for the circumstances. - At a minimum, each QC program must include written procedures in detail on step-by-step procedures for each of the following: - Calibration of CEMS - CD determination and adjustment of CEMS - Preventive maintenance of CEMS (including spare parts inventory) - Data recording, calculations, and reporting - Accuracy audit procedures including sampling and analysis methods - Program of corrective action for malfunctioning CEMS |
| --- | --- |

| Slide 46 NOTE: RAA’s are not used very often, as CGAs are more commonly used. | Procedure 1 – Checks/Auditing Requirements Instructor Notes: - Explain checks/auditing requirements for Procedure 1. - Point out that one RATA is required at least every four calendar quarters, except where the affected facility is off-line (does not operate) in the fourth calendar quarter since the quarter of the previous RATA. If this occurs, the RATA shall be performed in the quarter in which the unit recommences operation. CGAs are not required for calendar quarters in which the affected facility does not operate. |
| --- | --- |

| Slide 47 | Procedure 1 – Performance Criteria Instructor Notes: - Explain performance criteria for Procedure 1. - Explain the concept of out-of-control (OOC): - During the period the monitor is OOC, the CEMS data may not be used in calculating emission compliance nor be counted towards meeting minimum data availability. - The beginning of the OOC period is the time corresponding to the completion of the sampling for the RATA, RAA, or CGA. If the CD criteria is exceeded by 4 times the criteria specified the OOC period begins at the time of the end of the preceding OOC check. - The end of the OOC period is the time corresponding to the completion of the sampling of the subsequent successful audit. - If CEMS is out-of-control, take necessary corrective action to eliminate the problem: - Following corrective action, the CEMS must be audited with a RATA, CGA, or RAA to determine if the CEMS is operating within the specifications. - A RATA must always be used following OOC period resulting from a RATA. IMPORTANT/KEY MESSAGE: - The CEMS operator shall report both the audit showing the CEMS to be OOC and the results of the audit following corrective action showing the CEMS to be operating within specifications. |
| --- | --- |

| Slide 48 | Commonly Used Technologies: Pulsed Fluorescence and Chemiluminescence Analyzer Instructor Notes: - Describe pulsed fluorescence and chemiluminescence analyzer. - In general, fluorescence absorbs light at one frequency, and emits light at another |
| --- | --- |

| Slide 49 | SO2 Analyzer Instructor Notes: - Describe the SO2 analyzer. |
| --- | --- |

| Slide 50 | SO2 Monitor Instructor Notes: - Review the components of the SO2 monitor. |
| --- | --- |

| Slide 51 | Chemiluminescence NOX Analyzer Instructor Notes: - Describe the chemiluminescence NOX analyzer. - Tell participants that it is a very common NOx analyzer. - Oxidation reaction is what causes chemiluminescence. NO reacts with O3—emitting energy in the form of light. The more NO reacting with O3, the more energy that you get out of it. |
| --- | --- |

| Slide 52 | How is NOX Measured? Instructor Notes: - Explain how NOX is measured. |
| --- | --- |

| Slide 53 | NOX Monitor Instructor Notes: - Review the components of the NOX monitor. |
| --- | --- |

| Slide 54 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 2. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-2.” ACTIVITY - Continue the game format for the knowledge check questions for PS-2. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 55 | PS-2 – Question 1 Instructor Notes: - During the PS-2 seven-day CD test, most plants must be operating more than _______% of normal plant load. Answer: D. No operating load is specified. PS-2 just states that the facility must be operating. However, this is not true for daily calibrations conducted under Procedure 1. Under Procedure 1, the unit does not have to be operating to conduct a daily calibration check. |
| --- | --- |

| Slide 56 | PS-2 – Question 2 Instructor Notes: - During preliminary stratification testing, you find the mean pollutant concentration varies by more than 10% difference for any one point. Is the source stratified or not stratified? Answer: A. The source is stratified |
| --- | --- |

| Slide 57 | PS-2 – Question 3 Instructor Notes: - The relative accuracy test audit, or RATA, must be passed prior to installation of the CEMS. Answer: B. False. The CEMS must be installed before certification testing can begin. |
| --- | --- |

| Slide 58 | Procedure 1 Instructor Notes: 1. Name three types of quarterly audits Answer: CGA – if applicable, may be conducted in three of four calendar quarters, but in no more than three quarters in succession RAA – may be conducted three of four calendar quarters, but in no more than three quarters in succession Other Alternative Audits – may be conducted as approved by the Administrator for three of four calendar quarters - When should a RATA be performed? Answer: One RATA is required at least every four calendar quarters, except where the affected facility is off-line (does not operate) in the fourth calendar quarter since the quarter of the previous RATA. If this occurs, the RATA shall be performed in the quarter in which the unit recommences operation - What are the QC requirements of Procedure 1? Answer: At a minimum, each QC program must include written procedures in detail on step-by-step procedures for each of the following: - Calibration of CEMS. - CD determination and adjustment of CEMS. - Preventive maintenance of CEMS (including spare parts inventory). - Data recording, calculations, and reporting. - Accuracy audit procedures including sampling and analysis methods. - Program of corrective action for malfunctioning CEMS. |
| --- | --- |

| Slide 59 | Performance Specifications 3 and 4 Instructor Notes: SAY: “Now, let’s discuss PS-3 and PS-4, which includes specifications and test procedures for oxygen and carbon dioxide CEMS in stationary sources.” |
| --- | --- |

| Slide 60 | Overview of PS-3 Instructor Notes: - Provide an overview of PS-3. |
| --- | --- |

| Slide 61 | Calibration Drift and Relative Accuracy Performance Criteria – PS-3 Instructor Notes: - Review CD and RA performance criteria for PS-3 |
| --- | --- |

| Slide 62 | Quality Assurance Procedure 1 Instructor Notes: - Discuss information on the slide pertaining to QA Procedure 1. |
| --- | --- |

| Slide 63 | Commonly Used Technologies for PS-3 Instructor Notes: - Describe the zirconium oxide O2 analyzer. - Explain that oxygen molecules tend to flow from the reference side with the highest concentration of O2 to the sample side with the lowest O2 concentration. Within the solid electrolyte, the flow of oxygen generates a voltage which is related to the concentration of O2 in the sample by the Nernst equation. |
| --- | --- |

| Slide 64 | Commonly Used Technologies for PS-3: O2 & CO2 Analyzer Instructor Notes: - Describe the O2 and CO2 analyzer. |
| --- | --- |

| Slide 65 | Commonly Used Technologies for PS-3: Paramagnetic O2 Analyzer and Non-Dispersive Infrared Instructor Notes: - Describe the paramagnetic O2 analyzer and the non-dispersive infrared (NDIR). |
| --- | --- |

| Slide 66 | Performance Specification 4 (PS-4) Instructor Notes: SAY: “Now, let’s discuss PS-4, which includes specifications for carbon dioxide CEMS in stationary sources.” |
| --- | --- |

| Slide 67 | Overview of PS-4 Instructor Notes: - Provide an overview of PS-4. |
| --- | --- |

| Slide 68 | Calibration Drift and Performance Specification Criteria – PS-4 Instructor Notes: - Review calibration drift and relative accuracy for PS-4 |
| --- | --- |

| Slide 69 | Quality Assurance - Procedure 1 Instructor Notes: - Discuss information on the slide pertaining to QA Procedure 1 |
| --- | --- |

| Slide 70 | Commonly Used Technology for PS-4 Instructor Notes: - Describe the gas filter correlation method. - Explain that the difference in the alternating infrared (IR) signal is due to the concentration of the gas in the sample. The IR light passing through this gas is already absorbed before reaching the sample gas cell. - Explain that the IR beam passes through the rotating wheel including the section with the gas, causing an alternating IR spectrum which then passes through the sample gas cell and is read by the detector. |
| --- | --- |

| Slide 71 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 3. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-3 and PS-4.” ACTIVITY - Continue the game format for the knowledge check questions for PS-3 and PS-4. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 72 | PS-3 Instructor Notes: - For PS-3, CEMS calibration must not drift by more than ______ O2 or CO2 from the reference value. Answer: B. For PS-3, CEMS calibration must not drift by more than 0.5% O2 or CO2 from the reference value. - Name three commonly used O2/CO2 analyzer technologies. Answer: Three commonly used O2/CO2 analyzer technologies are paramagnetic, zirconium oxide, and NDIR. - The results of a RATA are considered valid if the calculated relative accuracy is less than ____ , or if the RA is less than or equal to _____ when the applicable emission standard is used. Answer: A. The results of a RATA are considered valid if the calculated relative accuracy is less than 20.0%, or if the RA is less than or equal to 1.0% when the applicable emission standard is used. |
| --- | --- |

| Slide 73 | PS-4 – Question 1, 2 Instructor Notes: - For PS-4, CEMS calibration must not drift by more than _____CO from the reference value. Answer: D. For PS-4, CEMS calibration must not drift by more than 5% CO from the reference value. - For PS-4, the results of a RATA test are considered valid if the calculated relative accuracy is less than ____, or if the RA is less than or equal to ____ when the applicable emission standard is used. Answer: A. For PS-4, the results of a RATA test are considered valid if the calculated relative accuracy is less than 10%, or if the RA is less than or equal to 5% when the applicable emission standard is used. |
| --- | --- |

| Slide 74 | PS-4 – Question 3, 4 Instructor Notes: - Name two commonly used CO analyzer technologies. Answer: Two commonly used CO analyzer technologies are IR and GFC. - PS-4 was primarily written to be used for CO analyzers with what span? Answer: PS-4 was primarily written to be used for CO analyzers with a 1000 ppmv |
| --- | --- |

| Slide 75 | Performance Specification – 4A (PS-4A) Instructor Notes: SAY: “Now, let’s move on to PS-4A, which includes specifications and test procedures for carbon monoxide CEMS in stationary sources.” |
| --- | --- |

| Slide 76 | PS – 4A Overview Instructor Notes: - Provide an overview of PS-4A. SAY: “The slides that follow will include specific details on response time.” |
| --- | --- |

| Slide 77 | PS – 4A Requirements Instructor Notes: - Highlight the requirements for PS-4A. |
| --- | --- |

| Slide 78 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 4. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-4A.” ACTIVITY - Continue the game format for the knowledge check questions for PS-4A. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 79 | PS-4A Instructor Notes: - For PS-4A, the results of a RATA test are considered valid if the calculated RA is less than ____, or if the RA is less than or equal to ____ when the applicable emission standard is used. Answer: A. For PS-4A, the results of a RATA test are considered valid if the calculated RA is less than 10%, or if the RA is less than or equal to 5% when the applicable emission standard is used. - Name three reference methods that are associated with PS-4A. Answer: Three reference methods associated with PS-4A are M10, 10A, and 10B. - PS-4A was primarily written to be used for CO analyzers with what span? Answer: PS-4A was primarily written to be used for CO analyzers with less than 200 ppmv. |
| --- | --- |

| Slide 80 | Performance Specification 4B (PS-4B) Instructor Notes: SAY: “Now, let’s discuss PS-4B, which includes specifications and test procedures for carbon monoxide and oxygen CEMS in stationary sources.” |
| --- | --- |

| Slide 81 | PS-4B Overview Instructor Notes: - Provide an overview of PS-4B. - Explain that the definitions, installation and measurement location specifications, test procedures, data reduction procedures, reporting requirements, and bibliography are the same as in PS-2, PS-3 (for O2) and PS-4A (for CO), except as otherwise noted in the slides that follow. |
| --- | --- |

| Slide 82 | Performance and Equipment Specifications: Data Recorder Scale: O2 and Data Recorder Scale: CO Instructor Notes: - Provide performance and equipment specifications for the data recorder scale: O2 and data recorder scale: CO. |
| --- | --- |

| Slide 83 | Performance and Equipment Specifications: Calibration Drift and Calibration Error Instructor Notes: - Provide performance and equipment specifications for calibration drift and calibration error. |
| --- | --- |

| Slide 84 NOTE: ≤10% (if average RM value is used to calculate RA) ≤ 5% (if applicable emission standard used to calculate RA) Within 5 ppm when RA calculated as absolute average difference between RM and CEMS plus the 2.5% confidence coefficient | Performance and Equipment Specifications: Relative Accuracy: CO and O2 Instructor Notes: - Provide performance and equipment specifications for relative accuracy: CO and O2. |
| --- | --- |

| Slide 85 | Alternative Relative Accuracy Procedures Instructor Notes: - Explain alternative RA procedures. - Explain that a status check looks at the following: - Mechanically operated functions including mirror movements, zero pipe operation, calibration gas valve operations, etc. - Data acquisition/data reduction functions - Timing mechanism functions - Sample filters - Sample line heaters - Moisture traps - Light source - Signal receiver - Data recorders |
| --- | --- |

| Slide 86 | Quality Assurance Procedure 1 and Commonly Used Technology Instructor Notes: - Discuss information on the slide pertaining to QA Procedure 1 and commonly used technology, GFC, for PS4-B. |
| --- | --- |

| Slide 87 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 5. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-4B.” ACTIVITY - Continue the game format for the knowledge check questions for PS-4B. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 88 | PS-4B – Question 1, 2 Instructor Notes: - PS-4B is primarily used for testing what two pollutants together? Answer: PS-4B is primarily used for testing O2 and CO together. - For PS-4B, the results of a RATA test are considered valid if the calculated RA is less than ____, or if the RA is less than or equal to ____ when the applicable emission standard is used. Answer: A. For PS-4B, the results of a RATA test are considered valid if the calculated RA is less than 5.0%, or if the RA is less than or equal to 0.5% when the applicable emission standard is used. |
| --- | --- |

| Slide 89 | PS-4B – Question 3, 4 Instructor Notes: - For PS-4B CE, the mean difference between CEMS and reference values at all 3 test points must be less than or equal to 0.5% for which pollutant(s)? Answer: B. O2 - What is one commonly used technology associated with PS-4B? Answer: GFC is one commonly used technology associated with PS-4B. |
| --- | --- |

| Slide 90 | Performance Specification 5 (PS-5) Instructor Notes: SAY: “Now, let’s discuss PS-5, which includes specifications and test procedures for total reduced sulfur CEMS in stationary sources.” |
| --- | --- |

| Slide 91 | PS-5 Overview Instructor Notes: - Provide an overview of PS-5. - Explain that total reduced sulfur (TRS) CEMS may include O2 monitors when regulations specify that the TRS concentrations must be corrected to a specified O2 concentration (i.e., 20 ppm @ 7% O2). |
| --- | --- |

| Slide 92 | Calibration Drift and Relative Accuracy Instructor Notes: - Provide calibration drift and relative accuracy test information. - Explain that during an RA test, the testing consultant may perform any number of runs over the 9-run minimum. However, only 3 runs may be discarded, and all remaining runs must be used to calculate the RA. - If 12 runs, may discard 3 and use 9 - If 10 runs, may only discard 1 run and use 9 - Tell participants that both the TRS and O2 CEMS must pass an initial RA test and a 7-day drift test. |
| --- | --- |

| Slide 93 | Commonly Used Technology for PS-5 Instructor Notes: - Describe a gas chromatography. - Tell participants that oxidation techniques are also used. |
| --- | --- |

| Slide 94 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 6. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-5.” ACTIVITY - Continue the game format for the knowledge check questions for PS-5. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 95 | PS-5 Instructor Notes: - What are three reference methods that are commonly associated with PS-5? Answer: The three reference methods that are commonly associated with PS-5 are 16, 16A, and 16B. 2. For PS-5, the results of a RATA test are considered valid if the calculated RA is less than ____ , or if the RA is less than or equal to ____ when the applicable emission standard is used. Answer: C. For PS5, the results of a RATA test are considered valid if the calculated RA is less than 20%, or if the RA is less than or equal to 10% when the applicable emission standard is used. |
| --- | --- |

| Slide 96 | Performance Specification 6 (PS-6) Instructor Notes: SAY: “Now, let’s discuss PS-6, which includes specifications and test procedures for continous emission rate monitoring systems CERMS in stationary sources.” |
| --- | --- |

| Slide 97 | Overview of PS-6 Instructor Notes: - Provide an overview of PS-6. IMPORTANT/KEY MESSAGE: - Explain that continuous emission rate monitoring systems (CERMS) includes the gas analyzers and the flow rate sensor(s) needed to determine the pollutant mass emission rate. The CERMS is the total equipment needed to calculate the pollutant mass emission rate. CERMS are basically CEMS with a flow rate sensor. |
| --- | --- |

| Slide 98 | Calibration Drift Instructor Notes: - Describe CD. - Explain that the flow rate sensor shall have provisions to check the CD for each flow rate parameter that it measures individually (e.g. velocity, pressure), as well as pollutant measurement analyzers (these must comply with specifications in the appropriate PS). - Tell participants that the CD for each pollutant analyzer uses the criteria established by the applicable PS (e.g., PS-2 for SO2 and NOX). |
| --- | --- |

| Slide 99 NOTE: Unless otherwise specified, the RM for the pollutant gas is the Appendix A method that is cited for compliance test purposes, or its approved alternatives. Methods 2, 2A, 2B, 2C, or 2D, as applicable, are the RMs for the determination of volumetric flow rate. | Relative Accuracy Instructor Notes: - Describe the RA of CERMS. |
| --- | --- |

| Slide 100 | Commonly Used Technologies for PS-6 Instructor Notes: - Describe pitot tubes. - Explain that the pitot tube is used to measure stack gas velocity. - Mention that the pitot tubes have small holes, and can get plugged with PM easily - Give information about Type S Pitot Tube (EPA Ref. Method 2) and Standard Pitot Tube: - Type S Pitot Tube: - Compact: Fits easily into stack sampling port - Durable: Withstand harsh stack environment and maintain calibration - Gives high manometer readings - Better at low velocities than Standard Pitot Tube - Standard Pitot Tube: - Calibration factor of .98 to 1.0 - Often used to calibrate the Type S pitot tube - Not used for source testing because the static port can be easily clogged with PM |
| --- | --- |

| Slide 101 | Commonly Used Technologies for PS-6 (Cont’d) Instructor Notes: - Describe the ultrasonic flowmeter. - Explain that acoustic velocimetry uses ultrasonic pulses to measure the velocity of the stack gases. A sound pulse traveling with the flow in stack will be accelerated by the gas and particulate matter (PM) flow. Conversely, a pulse traveling against the flow will be slowed. This doppler shift is similar to listening to a train approach and pass. The whistle will change in pitch in proportion to the speed of the train. |
| --- | --- |

| Slide 102 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 7. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-6.” ACTIVITY - Continue the game format for the knowledge check questions for PS-6. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 103 | PS – 6 Instructor Notes: 1. What is PS-6 primarily used for to perform? Answer: PS-6 is primarily used to perform CERMS installation and certification. 2. For PS-6, CERMS calibration must not drift by more than ___% from the reference value. Answer: A. 3% - What reference methods are used for determining flow under PS-6? Answer: Reference methods 2, 2A, 2B, 2C, and 2D are used for determining flow under PS-6. - When measuring flow rates, what are two commonly used techniques? Answer: When measuring flow rates, pilot tubes and ultrasonic flow meters are two commonly used techniques. |
| --- | --- |

| Slide 104 | Performance Specification 7 (PS-7) Instructor Notes: SAY: “Now, let’s discuss PS-7, which includes specifications and test procedures for hydrogen sulfide CEMS in stationary sources.” |
| --- | --- |
| Slide 105 | PS-7 Overview Instructor Notes: - Provide an overview of PS-7. |

| Slide 106 NOTE: Subparts or regulations may require on- going QA. | PS-7 Calibration Drift and Relative Accuracy Instructor Notes: - Explain CD and RA. |
| --- | --- |

| Slide 107 | Commonly Used Technology for PS-7 Instructor Notes: - Remind participants this was previously described in PS-5. |
| --- | --- |

| Slide 108 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 8. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-7.” ACTIVITY - Continue the game format for the knowledge check questions for PS-7. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 109 | PS-7 Instructor Notes: - What is PS-7 primarily used to certify? Answer: PS-7 is primarily used for certifying H2S CEMS - What reference methods are associated with PS-7? Answer: Reference methods 11, 15, and 16 are associated with PS-7. - What is a commonly used technology that is associated with PS-7? Answer: A GC is a commonly used technology associated with PS-7. |
| --- | --- |

| Slide 110 | Performance Specification 8 (PS-8) Instructor Notes: SAY: “Now, let’s discuss PS-8, which includes specifications and test procedures for volatile organic compounds CEMS in stationary sources.” |
| --- | --- |

| sSlide 111 | PS-8 Overview Instructor Notes: - Provide an overview of PS-8. |
| --- | --- |

| Slide 112 | PS-8 Calibration Drift and Relative Accuracy Instructor Notes: - Explain CD and RA. - Explain that during the RATA, if test values indicate that emissions are less than 50% of standard, the applicable standard to determine RA may be used. |
| --- | --- |

| Slide 113 | Commonly Used Technology for PS-8 Instructor Notes: - Describe the flame ionization detector (FID). |
| --- | --- |

| Slide 114 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 9. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-8.” ACTIVITY - Continue the game format for the knowledge check questions for PS-8. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 115 | PS-8 – Question 1, 2 Instructor Notes: Instructor Notes: - What is PS-8 primarily used to evaluate? Answer: PS-8 is primarily used to evaluate CEMS that measures a mixture of VOC. - For PS-8, CEMS calibration must not drift by more than ___% from the reference value. Answer: B. 2.5% |
| --- | --- |

| Slide 116 | PS-8 – Question 3, 4 Instructor Notes: - For PS-8, the results of a RATA test are considered valid if the CEMS is no greater than ___ % of the mean value of the RM data, or if the applicable emission standard calculation is less than or equal to ____ %. Answer: C. For PS-8, the results of a RATA test are considered valid if the CEMS is no greater than 20% of the mean value of the RM data, or if the applicable emission standard calculation is less than or equal to 10%. - What is the most commonly used technology associated with PS-8? Answer: The most commonly used technology associated with PS-8 is an FID. |
| --- | --- |

| Slide 117 | Performance Specification 8A (PS-8A) Instructor Notes: SAY: “Now, let’s discuss PS-8A, which includes specifications and test procedures for total hydrocarbons CEMS in stationary sources.” |
| --- | --- |

| Slide 118 | PS-8A Overview Instructor Notes: - Provide an overview of PS-8A. - Explain that PS-8A is one of the few performance specifications that are not technology neutral. It specifies a technology – FID. |
| --- | --- |

| Slide 119 | PS-8A Requirements Instructor Notes: - Discuss the PS-8A requirements. - Explain that CD is based on a 7-day period. If any 24-hour drift does not meet the criteria, diagnose and fix the problem and repeat the CD test. - Tell participants that a CE test must be performed through the entire sampling system and must not exceed 3% of the CEM span. |
| --- | --- |

| Slide 120 | Commonly Used Technology for PS-8A Instructor Notes: - Remind participants this was previously described in PS-8. |
| --- | --- |

| Slide 121 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 10. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-8A.” ACTIVITY - Continue the game format for the knowledge check questions for PS-8A. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 122 | PS-8A Instructor Notes: - What is PS-8A primarily used to evaluate? Answer: PS-8A is primarily used to evaluate one THC CEMS. - For a PS-8A calibration drift test, the CEMS must not drift by ____ppm or ___% of span value after each 24-hour period of the 7-day drift test for both the zero and span gases. Answer: D. For PS-8A calibration drift test, the CEMS must not drift by +3 ppm or +3 % of span value after each 24-hour period of the 7-day drift test for both the zero and span gases. |
| --- | --- |
| Slide 123 | Performance Specification 9 (PS-9) Instructor Notes: SAY: “Now, let’s discuss PS-9, which includes specifications and test procedures for gas chromatography CEMS in stationary sources.” |

| Slide 124 | PS-9 Overview Instructor Notes: - Provide an overview of PS-9. - Tell participants that this is also one of the few performance specifications that are not technology neutral. |
| --- | --- |

| Slide 125 | Sample Collection, Preservation, Storage and Transport Instructor Notes: - Describe location and measurement location specifications and the pre-test preparation period. |
| --- | --- |

| Slide 126 | Performance Audits and Calibration Instructor Notes: - Explain performance audits and calibration as it relates to PS-9. - Explain that performance audits and multi-point calibration are two separate things. Performance audits are comprised of a mid-level calibration gas injected three times through the sample transport system. Multi-point calibrations are comprised of low, mid, and high-level calibration gases injected in triplicate (PS-9 Section 10.2) directly to the instrument, unless the applicable permit or rule directs differently. As such, these tests are not the same, and both must be performed. - Explain that the initial multi-point calibration should be performed on Day 0 and on each of the subsequent 7 days. The instrument set points are set on Day 0 and do not necessarily have to be reset on the subsequent 7 days prior to each 24-hour period (similar to other performance specifications, such as PS-2, in which the calibration can be reset immediately after error is determined and prior to the next 24-hour period). |
| --- | --- |

| Slide 127 | Calibration Error Instructor Notes: - Explain CE as it relates to PS-9. |
| --- | --- |

| Slide 128 | Commonly Used Technology for PS-9 Instructor Notes: - Remind participants this was previously described in PS-7. |
| --- | --- |

| Slide 129 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 11. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-9.” ACTIVITY - Continue the game format for the knowledge check questions for PS-9. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 130 | PS-9 Instructor Notes: - PS-9 applies to CEMS that use___. Answer: PS9 applies to CEMS that use GC to measure gaseous organic compound emissions. |
| --- | --- |

| Slide 131 | Performance Specification 11 (PS-11) Instructor Notes: SAY: “Now, let’s discuss PS-11, which includes specifications and test procedures for particulate matter CEMS in stationary sources.” |
| --- | --- |

| Slide 132 | PS-11 Overview Instructor Notes: - Provide an overview of PS-11. - Explain that PS-11 is different from other performance specifications. It is based on a technique of correlating PM CEMS responses relative to emission concentrations determined by the reference method. This technique is called “the correlation.” - Tell participants that this differs from CEMS used to measure gaseous pollutants that have available calibration gases of known concentration. Because the type and characteristics of PM vary from source to source, a single PM correlation, applicable to all sources, is not possible. |
| --- | --- |

| Slide 133 | Installation and Performance Instructor Notes: - Describe installation and performance required for evaluating the acceptability of a PM CEMS. |
| --- | --- |

| Slide 134 | Drift and Correlation Test Instructor Notes: - Describe the drift and correlation test. |
| --- | --- |

| Slide 135 | Performance Test Instructor Notes: - Describe performance test requirements. |
| --- | --- |

| Slide 136 | Developing a PS-11 Correlation Instructor Notes: - Discuss developing a PS-11 correction. - Explain that 15 sets or more of CEMS and reference method measurements may be conducted. If this option is chosen, one may reject certain test results so long as the total number of valid test results used to determine the correlation is greater than or equal to 15. |
| --- | --- |

| Slide 137 | Procedure 2 – Quality Assurance Requirements for Particulate Matter CEMS At Stationary Sources Instructor Notes: - Describe the three basic functions of Procedure 2. |
| --- | --- |

| Slide 138 | Procedure 2 – Quality Control Program Instructor Notes: - Describe procedures for a QC program. |
| --- | --- |

| Slide 139 | Procedure 2 – Auditing Requirements Instructor Notes: 1. Describe Procedure 2, auditing requirements. 2. Explain the difference between sample volume check and sample volume audits (SVA). |
| --- | --- |

| Slide 140 | Procedure 2 – Performance Criteria Instructor Notes: - Describe Procedure 2, performance criteria. |
| --- | --- |

| Slide 141 | Procedure 2 – Performing Response Correlation Audit Performance Criteria Instructor Notes: - Describe Procedure 2, performing response correlation audit performance criteria. - Explain that the specified area on the graph of the correlation regression line is defined by two lines parallel to the correlation regression line, offset at a distance of ±25% of the numerical emission limit value from the correlation regression line. - Tell participants that if any of the PM CEMS response values resulting from your response correlation audit (RCA) are lower than the lowest PM CEMS response value of your existing correlation curve, you may extend your correlation regression line to the point corresponding to the lowest PM CEMS response value obtained during the RCA. This extended correlation regression line must then be used to determine if the RCA data meets this criterion. |
| --- | --- |

| Slide 142 | Procedure 2 – Relative Response Audit Performance Criteria Instructor Notes: - Describe Procedure 2, relative response audit performance criteria. - Explain that if your PM CEMS is OOC: - You must take necessary corrective action to eliminate the problem and perform tests, as appropriate, to ensure that the corrective action was successful. - You must report both the audit showing your PM CEMS to be out of control and the results of the audit following corrective action showing your PM CEMS to be operating within specifications. |
| --- | --- |

| Slide 143 | Commonly Used Technologies for PS-11 Instructor Notes: - Describe light scattering PM CEMS and a beta gauge PM CEMS. |
| --- | --- |

| Slide 144 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 12. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-11.” ACTIVITY - Continue the game format for the knowledge check questions for PS-11. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 145 | PS-11 – Question 1, 2 Instructor Notes: - PS-11 is primarily used for certifying _____. Answer: PS-11 is primarily used for certifying PM CEMS. - How does PS-11 differ from other performance specifications? Answer: A. Type and characteristics of PM vary from source to source. |
| --- | --- |

| Slide 146 | PS-11 – Question 3, 4 Instructor Notes: - What are two commonly used measurement techniques for PM CEMS? Answer: - Which procedure is associated with PS-11? Answer: Procedure 2 is associated with PS-11. |
| --- | --- |

| Slide 147 | Performance Specification 12A (PS-12A) Instructor Notes: SAY: “Now, let’s discuss PS-12A, which includes specifications and test procedures for total vapor phase mercury CEMS in stationary sources.” |
| --- | --- |

| Slide 148 | PS -12A Overview Instructor Notes: - Provide an overview of PS-12A. - Explain that mercury monitoring approaches not entirely suited to these specifications may be approvable under the alternative monitoring or alternative test method provisions of §60.13(i) and §63.8(f) or §60.8(b)(3) and §63.7(f), respectively. - Explain that the main difference between 12A and 12B is that 12A is instrumental and 12B is a sorbent trap CEMS. |
| --- | --- |

| Slide 149 | PS -12A Overview (Cont’d) Instructor Notes: - Continue providing an overview of PS-12A. |
| --- | --- |

| Slide 150 | Measurement Error and Calibration Drift Instructor Notes: - Describe the ME and CD test as it relates to PS-12A. |
| --- | --- |

| Slide 151 | Relative Accuracy and Reference Methods Instructor Notes: - Describe RA and reference methods as it relates to PS-12A. - Explain that: - If RM 29, RM 30B, or ASTM-D6784-02 are used, paired trains must be used. Calculate the relative deviation of paired samples. Note: - RD for any data pair must be <10% if Hg conc. >1.0 µg/m3 - RD for any data pair must be <20% if Hg conc. <1.0 µg/m3 - If moisture measurements are required; moisture and Hg measurements should be conducted simultaneously, or within an hour of Hg measurements. - Perform ongoing QA according to requirements of 40 CFR 60, Appendix F, Procedure 5. |
| --- | --- |

| Slide 152 | Procedure 5 - Quality Assurance Requirements for Vapor Phase Mercury CEMS and Sorbent Trap Monitoring Systems Used for Compliance Determination At Stationary Sources Instructor Notes: - Describe the basic functions of Procedure 5. |
| --- | --- |

| Slide 153 | Procedure 5: Quality Control Requirements Instructor Notes: - Describe Procedure 5, QC minimum requirements. - Explain that these written procedures must be kept on record and available for inspection by the responsible enforcement agency. - Explain that if excessive inaccuracies of an Hg CEMS occur for two consecutive quarters, QA/QC procedures must be revised or the CEMS modified or replaced (necessitating the CEMS be recertified). |
| --- | --- |

| Slide 154 | Procedure 5: Calibration Drift Assessment Instructor Notes: - Describe Procedure 5, CD assessment. |
| --- | --- |

| Slide 155 | Procedure 5: Data Accuracy Assessment Instructor Notes: - Describe Procedure 5, data accuracy assessment. |
| --- | --- |

| Slide 156 | Procedure 5: Excessive Audit Inaccuracy Instructor Notes: - Describe Procedure 5, excessive audit inaccuracy. - Explain that excessive audit inaccuracy refers to: - When the results of RATA, QGA, or RAA exceed criteria in 5.3.3 - The CEMS or sorbent trap monitoring system in out of control - Tell participants that should this occur: - Take necessary steps to correct the problem and follow corrective actions. - The CEMS must be audited using the same test that failed to meet the accuracy criterion; both the results of the failed test and results of retest must be reported. |
| --- | --- |

| Slide 157 | Commonly Used Technology for PS-12A Instructor Notes: - Describe atomic fluorescence spectroscopy. |
| --- | --- |

| Slide 158 | Hg CEMS Atomic Fluorescence Instructor Notes: - Describe Hg CEMS atomic fluorescence. |
| --- | --- |

| Slide 159 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 13. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of PS-12A.” ACTIVITY - Continue the game format for the knowledge check questions for PS-12A. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 160 | PS-12A – Question 1, 2 Instructor Notes: - PS-12-A is primarily used for certifying _____. Answer: PS-12A is primarily used for certifying total vapor phase (gas-phase elemental and oxidized) Hg CEMS. - The results of a RATA test are considered valid if the calculated RA is less than ____ , or if the absolute difference is less than or equal to ____ ug/m3. Answer: The results of a RATA test are considered valid if the calculated RA is less than 20%, or if the absolute difference is less than or equal to 1.0% ug/m3. |
| --- | --- |

| Slide 161 | PS-12A – Question 3, 4 Instructor Notes: - What reference methods are commonly associated with PS-12A? Answer: Reference methods M29, 30A, 30B, and ASTM 6784 are commonly associated with PS-12A. - What are two measurement techniques used for PS-12A? Answer: Sorbent traps and atomic fluorescent spectroscopy are two measurement techniques used for PS-12A. |
| --- | --- |

| Slide 162 | Performance Specification 12B (PS-12B) Instructor Notes: SAY: “Now, let’s discuss PS-12B, which includes specifications and test procedures for total vapor phase mercury using sorbent traps in stationary sources.” |
| --- | --- |

| Slide 163 | PS-12B Overview 1 Instructor Notes: - Provide an overview of PS-12B. |
| --- | --- |

| Slide 164 | PS-12B Overview 2 Instructor Notes: - Continue overview of PS-12B. |
| --- | --- |

| Slide 165 | PS-12B Relative Accuracy and Reference Methods Instructor Notes: - Discuss RA and RMs associated with sorbent trap monitoring systems. |
| --- | --- |

| Slide 166 | Quality Assurance/Quality Control Criteria for Sorbent Trap Monitoring Systems Instructor Notes: - Discuss QA/QC criteria for sorbent trap monitoring systems. |
| --- | --- |

| Slide 167 | Relative Deviation, Quality Assurance/Quality Control Instructor Notes: - Discuss relative deviation, QA/QC for sorbent traps. |
| --- | --- |

| Slide 168 | Quality Assurance/Quality Control Instructor Notes: - Highlight details on the slide regarding QA/QC for sorbent traps. |
| --- | --- |

| Slide 169 | Quality Assurance/Quality Control (Cont’d) Instructor Notes: - Continue reviewing details regarding QA/QC for sorbent traps. |
| --- | --- |

| Slide 170 | Common Technology Instructor Notes: - Describe sorbent traps and Hg. |
| --- | --- |

| Slide 171 | Sorbent Trap Monitoring System Background Instructor Notes: - Discuss the background of a sorbent trap monitoring system. - Note that the sample rate is proportional to the stack gas flow. - Discuss the need to be sure to check to see what spike recovery you get. |
| --- | --- |

| Slide 172 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 14. Let’s Test Your Knowledge! Instructor Notes: SAY: “Let’s test your knowledge of PS-12B.” ACTIVITY - Continue the game format for the knowledge check questions for PS-12B. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 173 | PS-12B – Question 1, 2, 3 Instructor Notes: - PS-12A and PS-12B differ because PS-12A is targeted specifically towards sorbent trap testing. Answer: False. - Pre- and post- leak checks are required for PS-12B sampling. Answer: True - A paired set of traps are used in the methodology of PS-12B. Answer: True |
| --- | --- |

| Slide 174 | PS-12B – Question 4 Instructor Notes: - What is the spike recovery requirement from section 3 of sorbent traps? Answer: A. 75-125% of spike amount |
| --- | --- |

| Slide 175 | Performance Specification 15 (PS-15) Instructor Notes: SAY: “Let’s discuss PS-15, which includes specifications and test procedures for extractive fourier transform infrared CEMS in stationary sources.” |
| --- | --- |

| Slide 176 | PS-15 Overview Instructor Notes: - Provide an overview of PS-15. - Tell participants that measuring may also be used for other criteria pollutants (i.e., NO, NO2, CO, H2O). |
| --- | --- |

| Slide 177 | What is Fourier Transform Infrared? Instructor Notes: - Describe a fourier transform infrared (FTIR) spectrometer. |
| --- | --- |

| Slide 178 | Fourier Transform Infrared System Requirements Instructor Notes: - Explain FTIR system requirements. - Tell participants that the calibration transfer standard (CTS) shows that a FTIR is working properly. |
| --- | --- |

| Slide 179 | Quality Assurance/Quality Control Instructor Notes: - Describe QA/QC checks. |
| --- | --- |

| Slide 180 | Calibration and Standardization Instructor Notes: - Explain the following information about calibration and standardization: - CTS: A well characterized absorbance band in the CTS gas is used to measure the path length and line resolution of the instrument. CTS measurements must agree within + 5% after pressure corrections. - Analyte Calibration: The method of determining the detector response to a known concentration of target compounds or pollutants. Use EPA library or prepare reference spectra. - System Calibration: Sampling system is purged with the calibration standard to verify that the absorbance measured is equal to the absorbance in the analyte calibration. - Analyte Spike: The target analyte(s) is spiked at the outlet of the sampling probe, upstream of the particulate filter, and combined with effluent at a ratio of about 1-part spike to 9 parts effluent. |
| --- | --- |

| Slide 181 | Analytical Procedure Instructor Notes: - Describe the analytical procedure in Section 6.0 FTIR protocol using validation and comparison to applicable RM. - Explain that SF6 (Sulfur Hexafluoride) is used to determine dilution ratio because it is not in the environment or to be found in the stack. Therefore, it is put in the analyte spiking gases to determine the dilution ratio. |
| --- | --- |

| Slide 182 | Analytical Procedure – 3 Methods Instructor Notes: - Explain the three methods for carrying out analytical procedures. - Tell participants that under method 3, each run is 1-hour and consists of at least 10 FTIR CEM measurements and 10 RM CEMS measurements. |
| --- | --- |

| Slide 183 | Absorbance Spectrum Measured by Fourier Transform Infrared Instructor Notes: - Explain the graph that shows the absorbance spectrum measured by FTIR. |
| --- | --- |

| Slide 184 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 15. Let’s Test Your Knowledge! Instructor Notes: SAY: “Let’s test your knowledge of PS-15.” ACTIVITY - Continue the game format for the knowledge check questions for PS-15. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 185 | PS-15 Instructor Notes: - What does the CEMS measure that PS-15 is used to certify? Answer: The CEMS measures all HAPs, as well as volatile organic and inorganic species. - Which EPA FTIR reference method is associated with PS-15? Answer: EPA FTIR reference method 301 is associated with PS-15. - Which technique is used by PS-15? Answer: B. FTIR is a technique used by PS-15. |
| --- | --- |

| Slide 186 | Performance Specification 16 (PS-16) Instructor Notes: SAY: “Let’s discuss PS-16, which includes specifications and test procedures for predictive emission monitoring systems in stationary sources.” |
| --- | --- |

| Slide 187 | What is a PEMS? Instructor Notes: - Describe predictive emission monitoring systems (PEMS). |
| --- | --- |

| Slide 188 | PS-16 Overview Instructor Notes: - Provide an overview of PS-16. |
| --- | --- |

| Slide 189 | PS-16 Overview (Cont’d) Instructor Notes: - Continue overview of PS-16. - Explain the following information: - Excess Emissions PEMS- 9 runs, 3-level RA test: 3 at each load level, total of 9 runs (at minimum) - Compliance PEMS- 27 runs, 3-level RA test: 9 runs at each load level, for three levels. Total of 27 runs (at minimum) - F-test: Comparison of paired data from RM and PEMS to determine if they differ by more than what might be expected from chance - Use equation 12.3.2 |
| --- | --- |

| Slide 190 | Initial Certification Instructor Notes: - Discuss details on initial certification. |
| --- | --- |

| Slide 191 | Initial Certification (Cont’d) Instructor Notes: - Continue discussion of initial certification. |
| --- | --- |

| Slide 192 | Ongoing Quality Assurance Tests Instructor Notes: - Discuss ongoing QA tests. |
| --- | --- |

| Slide 193 | Ongoing Quality Assurance Tests (Cont’d) Instructor Notes: - Continue discussion of ongoing QA tests. |
| --- | --- |

| Slide 194 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 16. Let’s Test Your Knowledge! Instructor Notes: SAY: “Let’s test your knowledge of PS-16.” ACTIVITY - Continue the game format for the knowledge check questions for PS-16. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 195 | PS -16 – Question 1, 2 Instructor Notes: - How does PEMS work? Answer: PEMS uses the continuous measurement of selected plant parameters and plant operating conditions with a software-based system of mathematical models to determine the pollutant emissions. - PS-16 is used for determining whether a PEMS is acceptable for use in demonstrating compliance with applicable requirements. Answer: True. PS-16 is used for determining whether a PEMS is acceptable for use in demonstrating compliance with applicable requirements. |
| --- | --- |

| Slide 196 | PS-16 – Question 3 Instructor Notes: - During initial testing, how many runs must be used for excess emissions monitor and compliance monitor? Answer: A. Excess - 9 runs; Compliance- 27 runs |
| --- | --- |

| Slide 197 | Performance Specification 18 (PS-18) Instructor Notes: SAY: “Let’s discuss PS-18, which includes specifications and test procedures for gaseous hydrogen chloride CEMS in stationary sources.” |
| --- | --- |

| Slide 198 | PS-18 Overview Instructor Notes: - Provide an overview of PS-18. |
| --- | --- |

| Slide 199 | Interference Test Instructor Notes: - Provide information about interference tests. |
| --- | --- |

| Slide 200 | Beam Intensity and Temperature Verification Instructor Notes: - Describe beam intensity and temperature verification. |
| --- | --- |

| Slide 201 | Pressure Verification and Level of Detection Instructor Notes: - Describe pressure verification procedure and level of detection determination. |
| --- | --- |

| Slide 202 | Response Time and Measurement Error Tests Instructor Notes: - Describe response time and ME tests. |
| --- | --- |

| Slide 203 | PS-18 Calibration Drift and Relative Accuracy Instructor Notes: - Describe the 7-day CD test and RA. |
| --- | --- |

| Slide 204 | Quality Assurance Procedure 6 Instructor Notes: - Describe the basic functions of Procedure 6. |
| --- | --- |

| Slide 205 | Procedure 6 Instructor Notes: - Discuss additional details pertaining to Procedure 6. |
| --- | --- |

| Slide 206 | Procedure 6 (Cont’d) Instructor Notes: - Continue discussing additional details pertaining to Procedure 6. |
| --- | --- |

| Slide 207 | Commonly Used Technologies for PS-18 Instructor Notes: - Describe a tunable diode laser spectroscopy. |
| --- | --- |

| Slide 208 | Commonly Used Technologies for PS-18 (Cont’d) Instructor Notes: - Describe cavity ring-down spectroscopy (CRDS). - Explain that at a preset level, the laser is turned off. The light within the cavity continues to bounce between the mirrors. However, because the mirrors have slightly less than 100% reflectivity, the light intensity inside the cavity steadily leaks out and decays to zero in an exponential fashion. - Explain that this decay, or "ring down", is measured in real-time by the photodetector. The amount of time it takes for the ring down to happen is determined solely by the reflectivity of the mirrors (for an empty cavity). This is then repeated with the target introduced into the cavity. The additional absorbance of the reflecting light by the gas accelerates the ring down time compared to a cavity without any absorption by the gas. The concentration of the gas is derived from the difference between these rings’ down times, and is therefore independent of laser intensity fluctuations or absolute laser power. |
| --- | --- |

| Slide 209 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 17. Let’s Test Your Knowledge! Instructor Notes: Instructor Notes: SAY: “Let’s test your knowledge of PS-18.” ACTIVITY - Continue the game format for the knowledge check questions for PS-18. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 210 | PS-18 Instructor Notes: - A CEMS that is certified using PS-18 measures what pollutant? Answer: A CEMS that is certified using PS-18 measures HCl. - RA must be established with what reference methods? Answer: RA must be established with reference methods 26A, 320, 321, or ASTM D6348-12. - What is the basic function of procedure 6? Answer: The basic function of procedure 6 is to ensure HCl CEMS data meets acceptable standards for determining compliance on an ongoing basis. - What are the common technologies used for PS-18? Answer: Common technologies used for PS-18 include a TDL, CRDS, and FTIR. |
| --- | --- |

| Slide 211 Purpose: To review the module content by recalling specific details about the specific performance specification learned in Module 3. Estimated Time: 45 minutes - 30 minutes in groups - 15 minutes in group debrief NOTE: While groups are working, instructors are encouraged to walk around and observe. | Optional Activity Instructor Notes: ACTIVITY – SMALL GROUPS - Conduct a Module 3 culminating group activity with participants called “Which Performance Specification is it?” Divide the class into groups of 3-5, depending on the number of participants in the class. - Hand out one flipchart page to each group. - In small groups, participants write five (5) details pertaining to various performances specifications on a flipchart. They should not identify which detail the PS pertains to. These five details may include such things as a commonly used technology or pollutant. - When groups have finished working, gather all flipchart pages from each group. - Present each group’s flipchart and other groups determine which PS aligns to each detail. - When completed, proceed to the Activity Debrief on the next slide. |
| --- | --- |

| Slide 212 | Activity Debrief Instructor Notes: - Pose the following questions to participants to discuss their learning experience following this exercise. ASK: - “What was one of the challenges of doing this activity?” - “What from the activity and discussion can you apply back to your work?” - “How does the information in this module promote value or benefit to your role on the job?” |
| --- | --- |

| Slide 213 | Module 3 Summary Instructor Notes: - To wrap-up Module 3, review the learning objectives. |
| --- | --- |