MODULE 4: AUDITS/INSPECTIONS AND ENFORCEMENT

# Module 4: Audits/Inspections and Enforcement

Module 4 Description:

In Module 4, participants will be provided an overview of audits and inspections used for CMS. They will learn about the types of audits and what is involved in an inspection. In addition, they will learn about preventative maintenance and failure, as well as enforcement.

Module 4 Learning Objectives:

- Distinguish the difference between performance audits and systems/field audits

- Explain the utility of performance audits and systems/field audits

- Describe the inspector’s role during an audit

- Describe the procedures necessary to use CMS data in determining compliance

- Assess daily, weekly, monthly, quarterly, and annual required preventative maintenance and QA requirements

- Distinguish between CMS as compliance method and CMS data as credible evidence

Module 4 Preparation:

- Provide post-it notes to each participant for knowledge check games.

- Provide a piece of paper for each participant for a culminating Module 4 group activity.

- Provide a piece of flipchart paper for each group for a culminating Module 4 group activity.

Estimated Time: 240 minutes (4 hours)

| Slide 1 | Module 4: Audits/Inspections and Enforcement Instructor Notes: SAY: “Module 4 is intended as an overview of audits, inspections, and enforcment of CMS. Let’s look more closely at the topics this module will cover.” |
| --- | --- |

| Slide 2 | Module 4 Outline Instructor Notes: - Review the topics covered in the Module 4 outline. |
| --- | --- |

| Slide 3 | Module 4 Learning Objectives Instructor Notes: SAY: “Here are the objectives that you should be able to accomplish after we complete this module.” - Read the Module 4 learning objectives. |
| --- | --- |

| Slide 4 | Overview of Audits and Inspections Instructor Notes: - Explain that there are two types of audits. SAY: “Cylinder Gas Audit or CGA, Relative Accuracy Test Audit or RATA, Relative Accuracy Audit or RAA, and Relative Correlation Audits or RCA, were previously covered in Module 3.” |
| --- | --- |

| Slide 5 | Performance and System Audits Instructor Notes: - Review the difference between a performance audit and a system or field audit. - Explain that EPA relies on a combination of performance and system/field auditing to verify overall data integrity. |
| --- | --- |

| Slide 6 | Performance Audits Instructor Notes: - Review the important features of performance audits. - Explain that there are several types of audits which facilities are required to undergo on a regular basis if they have a CEMS, COMS or PEMS. - Explain that the specifics of these audit requirements were covered in Module 3. |
| --- | --- |

| Slide 7 | System/Field Audit or Inspection Instructor Notes: - Explain that reviewing Part 75 information may be helpful to the inspector for creating an audit plan for their Part 60 source. |
| --- | --- |

| Slide 8 | System/Field Audit or Inspection Instructor Notes: - Review the inspector’s responsibilities in system/field audits. - Note that the “hands off” approach avoids creating a situation in which monitoring equipment may be damaged or the inspector's actions may be questioned should the monitoring system fail to operate well during the audit. |
| --- | --- |

| Slide 9 | Inspections: Before Going Onsite Instructor Notes: - Review how to prepare for an inspection before going onsite. - Explain that knowing the type of system (e.g., in situ or extractive), the key components, and how they are supposed to work, is essential to performing a thorough inspection. SHOW: - This is an animated slide, so each bullet will appear upon each click of the mouse. |
| --- | --- |

| Slide 10 | Inspections: Before Observing a Performance Audit Instructor Notes: - Review how to observe a performance audit during an inspection. SHOW: - This is an animated slide, so each bullet will appear upon each click of the mouse. |
| --- | --- |

| Slide 11 OPTIONAL KNOWELDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | - Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s participate in a game to test your knowledge of the information you’ve learned so far.” ACTIVITY - Divide class into groups with 3 or 4 participants per group. - Use the flipchart to capture team names and points. - Explain the directions to the participants: - The instructor will read the first knowledge check on the screen. Groups will quietly discuss their answer and raise their hand when they have an answer. - The instructor will call on the first group who raise their hands. - The instructor will record a point for each group/team that answers correctly. This game format continues for all the knowledge check questions. - Tell participants that this game will continue until the end of Module 4 since there are additional questions to come. Explain that those groups/teams who get the most points will receive a reward (e.g., extra break tomorrow). - Proceed to the following slides to conduct the activity. |
| --- | --- |

| Slide 12 | Audits/Inspections – Question 1 Instructor Notes: - True or False? The observer of an audit should move the CEMS analyzers in order to be able to verify their model and serial numbers. Answer: False. The auditor should not have any physical contact with the monitoring system hardware. |
| --- | --- |

| Slide 13 | Audits/Inspections – Question 2 Instructor Notes: - From the list below, which activity should not be done to prepare for an onsite visit? - Review records (e.g., monitoring plans, RATA, etc.) - Check data availability reports - Be prepared to provide technical advice or consulting on the operation of the monitors - Make note of any data errors or issues - Review previous audits - Review performance specifications and QA procedures, where relevant Answer: C. An inspector’s role is NOT to provide technical advice or consulting. |
| --- | --- |

| Slide 14 | Audits/Inspections – Question 3 Instructor Notes: - True or False? A systems/field audit should never be conducted during the same period a performance audit is being performed. Answer: False. A system audit can be done at same time as a performance audit. It is often more efficient to do so. |
| --- | --- |

| Slide 15 | Inspections Process – At the Facility Instructor Notes: - Review the inspections process at the facility. IMPORTANT/KEY MESSAGE: - Highlight that, if possible, arrive onsite for the inspection early enough to see the daily calibration, or request that the operator perform a manual calibration for you while you are there. |
| --- | --- |

| Slide 16 | Visual Inspection of the CEMS Instructor Notes: - Review the questions that should be answered during the inspection process at a facility. - Explain that analyzer pollutant and diluent concentration readings, and flow and pressure indications, should be recorded during the inspection in order to compare the readings to a prior inspection or to what is observed during a future inspection - Highlight that you should ask the CEMS operator to pull from historical CEMS data on the data acquisition system (DAS) several days of emissions data to compare to what was previously sent in the quarterly CEMS emission report. - Explain that while observing the calibration or performance test, the inspector should have the operator explain what he/she is doing and show the inspector where the procedure is documented. - This should include a discussion of the operator’s daily routine for maintaining the CEMS and how normal problems are handled. IMPORTANT/KEY MESSAGE: - Highlight that it is important for an inspector to observe how the CEMS operator performs his/her duties, as an indication that the plant personnel are following appropriate requirements and procedures |
| --- | --- |

| Slide 17 | Visual Inspection of the CEMS (Cont’d) Instructor Notes: - Continue to review the questions that should be answered during the inspection process at a facility. - Note that corrosion may be an indication of previous instances of condensed liquids. |
| --- | --- |

| Slide 18 | CEMS Shelter Instructor Notes: - Discuss the purpose of the CEMS shelter and how it relates to audits/inspections. - State that the CEMS shelter is temperature controlled. |
| --- | --- |

| Slide 19 | Calibration Gas Cylinders Instructor Notes: - Describe what calibration gas cylinders are and how they relate to audits/inspections. - State that from a safety perspective, it’s very important to strap or chain the canisters in. |
| --- | --- |

| Slide 20 | Pressure on Gas Cylinder Instructor Notes: - Describe what calibration gas cylinders are and how they relate to audits/inspections. |
| --- | --- |

| Slide 21 | CEMS Inspection Instructor Notes: - Discuss the components that need to be reviewed during a CEMS inspection. |
| --- | --- |

| Slide 22 | Measurement of Emissions Instructor Notes: - Discuss why it is important to ensure that the CEMS is installed in such a way that representative measurements of emissions are obtained, under the following scenarios: - The effluents are combined and subject to the same emissions standards. - The effluents are combined and not subject to the same emission standard. |
| --- | --- |

| Slide 23 | Measurement of Emissions (Cont’d) Instructor Notes: - Discuss why it is important to ensure that the CEMS is installed in such a way that representative measurements of emissions are obtained, under the following scenario: - The effluent from one affected facility is emitted from more than one emissions point. |
| --- | --- |

| Slide 24 | Who, What, Where, and Why Instructor Notes: - Discuss the importance of a pre-test meeting and review who should be at the test, what will happen, where the meeting will be held and why the meeting is necessary. - Highlight that a pre-test meeting can help you get ready for the performance specification test. - State that representatives from the CEM vendor and the state/local air agency should be present to observe and watch for problems. - Explain that the agency representative is particularly important because problems often occur during new plant start-ups that could require modification of the test plan or procedures. - Explain that the ability for the agency to approve or disapprove such changes is central to completing the test and avoids misunderstandings and rejected test data. |
| --- | --- |

| Slide 25 | The Road to Continuous Compliance: Operation of CEMS Instructor Notes: - Review what actions must be completed for continuous compliance operation of CEMS. - Explain that owners and operators of CEMS must check the zero (or low-level value between 0 and 20% of span value) and span (50 to 100% of span value) calibration drifts at least once each operating day in accordance with a written procedure. - The “span” is also called “high-level“ in Part 63 and has the same meaning. - Explain that the system must allow the amount of the excess zero and span drift to be recorded and quantified whenever specified. IMPORTANT/KEY MESSAGE: - Maintenance and operation include ensuring that necessary parts for routine repairs are readily available. |
| --- | --- |

| Slide 26 | Daily Data Readings Instructor Notes: - Describe how daily data readings are used in audits/inspections. - Explain that in general, the inspector should look at the computer screen for signs of a problem. In this example for NOx, all values in the “green” are in compliance with Part 75 and Part 60. The screen provides immediate feedback to the inspector by way of the “green” or “yellow” readings. A yellow reading may mean that the monitor is off-line or one of the readings is out of range. |
| --- | --- |

| Slide 27 | Road to Continuous Compliance Data Reduction Instructor Notes: - Review the calculation averages for continuous compliance including: - Operating Hours - What Valid Data Means - What is excluded - Explain that depending on the applicable subpart, hourly averages for certain partial operating hours are not computed or included in the emission averages. - For example, hours with < 30 minutes of unit operation for boilers subject to Subpart Db. - Explain that while most “non regular” data is excluded, some standards require that owners or operators include any data recorded during periods of monitor breakdown or malfunction. IMPORTANT/KEY MESSAGE: - Tell participants to review the specific regulation to which the source is subject for additional details. |
| --- | --- |

| Slide 28 | 1-Hour Average Validation Instructor Notes: - Discuss the 1-hour average validation as it relates to audits/inspections. |
| --- | --- |

| Slide 29 | Hourly Validation Example Instructor Notes: - Review the example of an hourly validation for an audit/inspection. |
| --- | --- |

| Slide 30 | Preventative Maintenance Examples Handout Instructor Notes: DIRECT: - Direct participants to the Preventative Maintenance Examples handout in their participant guide and ask them to briefly review. - Tell participants that this handout can be used as a resource and provides examples of preventative maintenance logs completed on a daily, weekly, monthly, and annual basis. - Ask participants if they have any questions about these examples. |
| --- | --- |

| Slide 31 OPTIONAL KNOWLEDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | 2. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s continue our game and continue testing your knowledge of Module 4.” ACTIVITY - Continue the game format for the knowledge check questions. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 32 | Audits/Inspections – Question 4 Instructor Notes: - Where should a CEMS be sited? Answer: CEMS must be installed so that representative measurements of emissions are obtained. |
| --- | --- |

| Slide 33 | Audits/Inspections – Question 5 Instructor Notes: - How is data from a CEMS reduced to 1-hour averages? Answer: For a full operating hour, at least four valid points are required to calculate the hourly average (i.e., one data point in each of the 15-minute quadrants of the hour). |
| --- | --- |

| Slide 34 | Audits/Inspections – Question 6 Instructor Notes: - What are some examples of parameters that an observer should be looking at for CEMS daily operations? Answer: Sample flow, gas pressure, and moisture (there are others) |
| --- | --- |

| Slide 35 | Use of CMS Data for Enforcement Instructor Notes: - Explain how CMS data is used for enforcement. |
| --- | --- |

| Slide 36 | Use of CMS Data for Enforcement (Cont’d) Instructor Notes: - Continue to explain how CMS data is used for enforcement. |
| --- | --- |

| Slide 37 | Enforcement Applications for CEMS Instructor Notes: - Review the enforcement applications of CEMS. - Tell participants that the next few slides will walk through these two enforcement applications. |
| --- | --- |

| Slide 38 | CMS is the Compliance Method Instructor Notes: - Explain the requirements when CMS is the compliance method. - Because CMS is the compliance method, we can rely on CMS data alone to prove a violation of the emissions standard in civil litigation. |
| --- | --- |

| Slide 39 | CMS is Not the Compliance Method Instructor Notes: - Provide the following information when CMS is not the compliance method: - CMS data may be used to issue a Notice or Finding of Violation or for negotiation in cases. - CMS data represents emissions comparable to the compliance method data, for example to determine magnitude and duration of emissions violations. - Regarding the “General Duty Clause,” Section 60.11(d) establishes a requirement for “good air pollution control practice for minimizing emissions.” CMS data may be used to ensure compliance with this requirement. |
| --- | --- |

| Slide 40 | 3. Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s continue our game and continue testing your knowledge of Module 4.” ACTIVITY - Continue the game format for the knowledge check questions. - Use the flipchart to continue to record a point to the group that answers a question correctly. |
| --- | --- |

| Slide 41 | Audits/Inspections – Question 7 Instructor Notes: - How can CMS be used to determine compliance with an emissions standard? Answer: CMS may be the compliance method specified in the rule or CMS may be used as credible evidence. |
| --- | --- |

| Slide 42 Purpose: To review the module content by enabling participants to summarize what they learned. Estimated Time: 40 minutes - 20 minutes in groups - 20 minutes in group debrief Preparation Checklist: - Provide a piece of a paper to each participant - Provide a piece of flipchart paper to each group. NOTE: While participants are working, instructor(s) are encouraged to walk around and observe. | Optional Activity: Geometric Close Instructor Notes: ACTIVITY – SMALL GROUPS - Conduct a Module 4 culminating group activity with participants called “Geometric Close.” - This activity could be optionally used to review all the course content for Modules 1-4. It can also be an individual activity as opposed to a group activity. - Divide the class into groups of 3-5, depending on the number of participants in the class. - Hand out a sheet of the paper to each participant. - Ask participants to individually take five minutes to write down: - One thing that “squared” with them (meaning a concept they learned today that they agree with – both sides of the square are even). - One thing that came full circle for them (one thing that they already knew that throughout the day was reinforced and confirmed what they already knew). - One thing they want to change (the triangle is a symbol for change). - Ask one participant in each group to draw a square, circle, and triangle on their piece of flipchart paper. - Ask participants to share their responses with their group and compile a consolidated list (within the shapes) on a piece of flipchart paper. - Encourage groups to post their “Geometric Close” answers on the flipchart paper at the front of the class. - Proceed to the Activity Debrief on the next slide. |
| --- | --- |

| Slide 43 | Activity Debrief Instructor Notes: - Ask each group for a volunteer to present their group’s answers to the rest of the class. |
| --- | --- |

| Slide 44 | Module 4 Summary Instructor Notes: - To wrap-up Module 4, review the learning objectives. |
| --- | --- |