UNITED STATES

ENVIRONMENTAL

PROTECTION AGENCY

# CONTINUOUS MONITORING SYSTEMS COURSE

iNSTRUCTOR gUIDE

TABLE OF CONTENTS

Getting Started	1

Course Overview	3

Course Description	3

Course Organization	3

Target Audience	3

Course Goals	4

Prerequisites	4

Evaluation	4

Class Size	4

Classroom Setup	5

Course Agenda	6

Tips and Reminders for Instructors	8

Classroom Tone	8

Course Schedule	8

Teaching Behaviors	9

During Facilitation	9

During Class Activities	9

Instructor Guide Administration	11

Features of the Instructor Guide	11

Icons and Associated Actions	11

Checklist of Training Materials	12

Course Introduction	15

Module 1: Introduction to CMS	24

Module 2: Overview of CMS and CMS Design and Components	54

Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies	91

Module 4: Audits/Inspections and Enforcement	212

LIST OF APPENDICES

APPENDIX A: Master Glossary

APPENDIX B: Master Resources

APPENDIX C: Pre and Post Self-Assessment

APPENDIX D: Course Exam

# Getting Started

Welcome to the Instructor Guide for the Continuous Monitoring Systems (CMS) Course. This Instructor Guide is intended to be a resource for you to use while you prepare and deliver the CMS course. You will use this Instructor Guide to create an engaging and informative experience for participants. This Instructor Guide includes:

- A course overview which provides information about the course content, target audience, class size, and classroom setup

- A Course Agenda

- Instructional tips to help you present the course effectively

- A list of Icons and Associated Actions which correspond to specific prompts in the instructor notes

- A Checklist of Training Materials for the course

- PowerPoint slides and accompanying instructor notes for each module*

- Appendices including a glossary, resource list, and handouts

You can modify the guide based on the needs and preferences of the participants that you will be teaching. For example, you can combine material from this course with other materials you may use. In addition, all activities and knowledge checks are optional to administer, as they may depend on audience mix. While customization is encouraged, it is recommended that you include the following as part of this course, each time it is delivered:

- Introductions – If it is the first time the group has been together, provide some time for introductions. Refer to the suggested introductions slide/icebreaker activity provided in the Course Introduction section below. If there are more than 20 participants, use a small group approach to introductions.

- Opening Activity – Some modules have an opening activity designed to review the previous day’s topics or to engage participants in the topics to be covered for the day.

- Explanation of the Materials – Provide participants with a quick orientation to any material you distribute. This would include the contents of their Participant Guide and any additional handouts.

*Note: Be sure to update the Instructors slide in the Course Introduction PowerPoint. Then, replace the slide thumbnail in the Instructor Guide and Participant Guide before printing the materials.

- Optional Self-Assessments – To determine the extent to which participants feel they have met the course objectives, consider administering a self-assessment to participants prior to and after the course. These self-assessments help participants establish a baseline of what they know prior to instruction and compare it to how they think their knowledge and skills have changed as a result of completing the course. The instructor(s) can also review the pre self-assessments to determine where there may be gaps in knowledge in order to focus on and highlight a particular content area in the curriculum. Refer to Appendix C: Pre and Post Self-Assessment.

- Optional Course Exam – Please coordinate directly with the sponsoring multi-jurisdictional organization (MJO) and/or state/local organization to discuss their preference for the course exam.  The course exam would be administered at the end of the training session, if desired. The purpose of the course exam is to assess participants’ understanding of the course content and their level of competency in applying what they learned. Refer to Appendix D: Course Exam.

It might be helpful to have two instructors present this course. At least one instructor will be a subject matter expert (SME) in CMS.

# Course Overview

## Course Description

The three-day classroom Continuous Monitoring Systems (CMS) Course provides participants with a basic understanding of CMS. It provides an overview of how to perform regulatory reviews and includes key concepts and information on CMS, including types, regulations, analytical techniques, systems design and components, performance specifications (PS), quality assurance (QA) requirements, commonly used technologies, audits/inspections, and enforcement procedures. In addition to the instructor presentation and lecture, participants have opportunities to apply their knowledge through practical exercises, facilitated discussions, and knowledge check games.

## Course Organization

There are four modules in this course and an introductory module:

- Course Introduction

- Module 1: Introduction to CMS

- Module 2: Overview of CMS and CMS Design and Components

- Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies

- Module 4: Audits/Inspections and Enforcement

## Target Audience

This course is intended for a fairly broad audience and could include participants with non-technical backgrounds (e.g., a basic degree in science) as well as technical backgrounds (e.g., a chemical engineering degree). No prior knowledge of CMS is presumed. This course is intended primarily for new hires or any participants who need an understanding of CMS in their job responsibilities.

Staff who could benefit from the course include, but are not limited to the following:

- Staff who are inspection and/or enforcement personnel

- Staff who observe stack test and CMS certifications

- Staff who are reviewing audit reports

- Staff who work on permits

## Course Goals

The CMS course has been designed as a three-day classroom immersion into:

- Key concepts pertaining to CMS

- Terminology and techniques that are common in the field

- Performance specifications and QA procedures

- How to use the performance specifications and where to locate requirements

- Different types of audits and enforcement procedures

## Prerequisites

There are no prerequisites for this course.

## Evaluation

The following types of evaluation will be conducted:

- Level 1 evaluation (reaction): accomplished through the use of the standard end-of-course evaluation

- Level 2 evaluation (learning): accomplished through the completion of post-training assessment and optional activities conducted throughout the course

## Class Size

Typically, class size should be limited to 30 participants or fewer to increase engagement, pace, and interaction among the facilitator(s) and participants.

## Classroom Setup

Depending upon how large the meeting room is, classroom seating may be all that is possible. However, if possible, arrange group seating at tables so that participants can share materials and ideas. It is ideal to create diverse groups with participants who have different levels of experience. This helps promote participant dialogue, foster collaboration, and provide a sense of support among the group members. Lastly, ensure:

- Furniture accommodates the participants comfortably

- There is accessible seating at some of the tables for any participants using a wheelchair or other mobility device

Distribute Participant Guides and any additional handouts at each table. Also, distribute any classroom supplies such as pens and pencils to each table. A full list of the training materials needed for this course can be found in the Checklist of Training Materials section of this guide.

## Course Agenda

| Scheduled Time | Module | Duration |
| --- | --- | --- |
| Day 1 |  |  |
| 8:30 am – 9:00 am | Course Introduction | 30 minutes |
| 9:00 am – 10:00 am | Module 1: Introduction to Continuous Monitoring Systems (CMS) | 60 minutes |
| 10:00 am – 10:30 am | Break | 15 minutes |
| 10:30 am – 12:00 pm | Continue Module 1: Introduction to Continuous Monitoring Systems (CMS) | 90 minutes |
| 12:00 pm – 1:00 pm | Lunch | 60 minutes |
| 1:00 pm – 1:30 pm | Wrap-up Module 1: Overview of the Course | 30 minutes |
| 1:30 pm – 2:00 pm | Module 2: Overview of CMS and CMS Design and Components | 30 minutes |
| 2:00 pm – 2:15 pm | Break | 15 minutes |
| 2:15 pm – 4:00 pm | Wrap-up Module 2: Overview of CMS and CMS Design and Components | 105 minutes |
|  | Total: | 435 minutes (7.5 hours) |
| Day 2 |  |  |
| 8:30 am – 10:00 am | Begin Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies | 90 minutes |
| 10:00 am – 10:15 am | Break | 15 minutes |
| 10:15 am – 12:00 pm | Continue Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies | 105 minutes |
| 12:00 pm – 1:00 pm | Lunch | 60 minutes |
| 1:00 pm – 2:00 pm | Continue Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies | 60 minutes |
| 2:00 pm – 2:15 pm | Break | 15 minutes |
| 2:15 pm – 4:00 pm | Continue Module 3: Performance Specifications, Quality Assurance, and Commonly Used Technologies | 105 minutes |
|  | Total: | 450 minutes (7.5 hours) |

| Day 3 |  |  |
| --- | --- | --- |
| 8:30 am – 9:45 am | Module 3 and Wrap Up: Performance Specifications, Quality Assurance, and Commonly Used Technologies | 75 minutes |
| 9:45 am –10:00 am | Break | 15 minutes |
| 10:00 am – 12:00 pm | Begin Module 4: Audits/Inspections and Enforcement | 120 minutes |
| 12:00 pm – 1:00 pm | Lunch | 60 minutes |
| 1:00 pm – 2:00 pm | Module 4: Audits/Inspections and Enforcement | 60 minutes |
| 2:00 pm – 3:00 pm | Course Wrap-up, Post-Training Assessment (optional) and Exam | 60 minutes |
|  | Total: | 390 minutes (6.5 hours) |

# Tips and Reminders for Instructors

Review the following instructional tips to help you present the course effectively.

## Classroom Tone

It is important to:

- Establish ground rules for the class that set the tone for the class.

- Maintain a positive, productive classroom environment.

- Model appropriate actions and responses. For example, your verbal and written instructions should be models for the groups. Giving specific instructions for completing an activity (e.g., walking through one example and writing a response on easel paper) and providing detailed sample responses will help the participants understand what is expected of them.

- Restrict the use of computers, phones, and other devices while class is in session.

## Course Schedule

As an instructor, it is important to adhere to the agenda and time schedule. However, adjust as necessary. You should not go too long without giving the participants a break. Refer to the Course Agenda. Although most participants will let you know when they need additional breaks, you should watch for nonverbal signs, including glazed eyes or shifting in seats, as indicators that a break is needed. Try to find natural breaking points in the course. Adjust the timing of breaks as necessary according to what is going on in the class. It is important to enforce break time limits. Resume training promptly at the end of a break.

## Teaching Behaviors

While teaching, share your diverse, “real-world” experiences, expertise, and knowledge throughout the course. As the instructor, you will lead and facilitate class discussions. When a participant asks you a question to which you do not know the answer, tell the participant you do not know the answer and explain that you will find the answer and get back to them. Although you should try to address most questions when they’re asked, utilize a “parking lot” technique to post participant questions that require later follow-up.

### During Facilitation

Although sticking to the agenda is important, you should not move to the next lecture or activity before ensuring that the group understands what has been discussed. It is important to check for understanding periodically. Here are some strategies you can use:

- Ask volunteers to tell you what they just heard or have them repeat what they learned to make sure you explained it clearly

- Ask volunteers how the information you just presented fits into what they already know or how it could be applied back on the job

During lectures, activities, and discussions, try not to separate yourself physically from the group by standing behind a podium, an overhead projector, or a table. You should feel free to walk around the room while you are speaking, engaging participants in the process.

### During Class Activities

During these optional class activities, it is important to observe how the groups work together and answer the following questions:

- Who participates most? Who participates least?

- Do certain participants try to dominate? Does anyone withdraw?

- Are there any negative undercurrents in the group?

- How do participants react to one another in small groups?

You should watch for both verbal and nonverbal responses and clues. Also, use your observations to keep the session running smoothly and share your observations with the group when appropriate.

Finally, remember that this Instructor Guide is a guide, not your script. You should feel free to modify discussion questions to meet the needs of your group. If a discussion question in this instructor guide does not work well into the flow of discussion in the classroom, modify it to suit the circumstances and enhance participant comprehension of the teaching points.

# Instructor Guide Administration

## Features of the Instructor Guide

This section provides the features and format of the Instructor Guide and provides explanations for the key icons used throughout the guide.

### Icons and Associated Actions

|  | SAY | This icon indicates a scripted narrative you can read verbatim, or you may choose to paraphrase. You speak these words to participants. Typically, this indicates a scripted transition between slides. |
| --- | --- | --- |
|  | ACTIVITY | This icon indicates you will be leading or facilitating an activity or discussion designed to help participants learn new information or practice a new skill. |
|  | ASK | This icon indicates that you will ask a question. |
|  | DIRECT | This icon indicates that you should direct the participants to a certain page or handout in the Instructor Guide. |
|  | SHOW | This icon indicates that you will show a resource, image, video, or equation, etc. |
|  | IMPORTANT/KEY MESSAGE | This icon indicates that you will emphasize or point out important or key information. |

### Checklist of Training Materials

This section provides a checklist of all materials required for the course (e.g., Participant Guide, handouts, audiovisual equipment, etc.). You will need the following materials and equipment to conduct this course. It is important to test all equipment prior to use to ensure it is functional and you are comfortable operating it.

- Instructor Guide, which is intended to be printed double-sided in color (one per instructor). This guide includes:

  - All course visuals

  - Notes and directions for the instructors, with icons and associated actions

  - Answer keys for knowledge check games

  - Suggested answers for discussion questions and activities

- Participant Guide, which is intended to be printed double-sided in color (one per participant). This guide includes:

  - All course visuals

  - Important/key messages

  - Space to take notes

- CMS Course PowerPoint files

  - There are five files for each module which are named:

    - Course Introduction__PPT_FINAL.pptx

    - Module 1_PPT_FINAL.pptx

    - Module 2_PPT_FINAL.pptx

    - Module 3_PPT_FINAL.pptx

    - Module 4_PPT_FINAL.pptx

- Handouts

  - The following handouts are available as part of this course:

    - General provisions

    - Properties of light

    - Performance testing

    - Commonly used technologies

    - Commonly used acronyms

    - Performance specifications

    - CMS definitions by performance specification (PS)

    - Preventative maintenance examples

- Appendices

  - APPENDIX A: Master Glossary

  - APPENDIX B: Master Resources

  - APPENDIX C: Pre and Post Self-Assessment

  - APPENDIX D: Course Exam

- Name tents for each participant

- Easel, chart paper, and markers for each table group and/or whiteboard, if provided

- Post-it notes for each table

- Masking tape for posting chart paper, if needed

- Computer projection system or overhead project

- Pens and pencils

NOTE:  Please refer to the introductory page for each module for any additional materials required per module.

COURSE INTRODUCTION

# Course Introduction

Course Introduction Description:

The course introduction serves as an overview of the CMS course. This overview includes the course goal, as well as an outline of the modules covered in the course. The course introduction also gives participants a chance to meet the instructors, as well as the other participants taking the course. Instructors also use this time to cover administrative aspects of the course including a review of the course materials and course agenda.

Course Introduction Preparation:

- Record instructor names and contact information on a flipchart page and post on the classroom wall.

- Title a flipchart page “Expectations.”

- Title a flipchart page “Parking Lot” and post on classroom wall.

- Title a flipchart page “Ground Rules.”

| Slide 1 NOTE: Engage and speak with participants who arrive early to help them feel at ease. It is not uncommon for people to arrive a little late on the first day; however, it’s important to balance this with respect for those who have arrived on time. A good way to manage this is to decide in advance when you will start on day 1 (maybe 15 minutes after the official start time). | WELCOME Instructor Notes: - Welcome the participants to the course as they enter the room. - When everyone is seated, begin the course by giving a formal welcome. SAY: “Welcome to the Continuous Monitoring Systems Course. We are so glad you are here. Let’s first begin with introducting ourselves, your instructors for this course.” |
| --- | --- |

| Slide 2 NOTE: In advance, record instructor names and contact information on a flipchart page and post on the classroom wall. | INSTRUCTORS Instructor Notes: - Introduce yourself. Say your name and job title, including perhaps where you work. Give some background information about yourself that pertains to your knowledge of the course subject matter. Also, relay an interest/hobby that you enjoy when not working. - Provide instructor contact information should participants need to contact you (e.g., emergency, etc.). |
| --- | --- |

| Slide 3 NOTE: If there is a large number of participants in the course, use a small group/pairs approach to the icebreaker activity. OPTIONAL ICEBREAKER ACTIVITY: Small Group/Partner Activity: Divide participants into small groups or pairs. Participants introduce themselves to their group or partner and come up with one question they would like answered following completion of the course. Instructors debrief as a whole class eliciting the participants’ questions and recording them on a flipchart titled “Parking Lot” in the front of the classroom. The goal is that all participants’ questions will be answered by the end of the course. Instructors should refer to these questions frequently throughout the course. For questions that cannot be answered, instructors should attempt to find the answers or make recommendations. | INTRODUCTIONS Instructor Notes: ACTIVITY – WHOLE-CLASS - Conduct an icebreaker activity for participants to introduce themselves. - Give instructions to participants for the activity. SAY: “On a post-it note, write what you hope or expect to accomplish in this course. Once you have completed this, we will go around the room and have everyone introduce themselves. Tell us your name, your job title, and then let us know your expectation about what you hope to accomplish from this course.” - Give participants about 5 minutes to write their expectation. - Begin participant introductions. - Take each participant’s post-it after his/her introduction and post it on the flipchart page “Expectations” in the front of the room. - Respond to the participants’ expectations. Explain whether the expectation will be met in this course. If not met in the course, provide or find out where the information might be best acquired. - Periodically, or at the end of the course, refer to these expectations to ensure they are being covered. |
| --- | --- |
| Slide 4 | COURSE INTRODUCTION Instructor Notes: - Explain the topics that will be covered during this course introduction. |

| Slide 5 | COURSE GOAL Instructor Notes: - Describe the course goal and the topics that will be covered in the course. |
| --- | --- |

| Slide 6 | COURSE OUTLINE Instructor Notes: - Review the course outline containing the titles of the four modules that are taught in this course. |
| --- | --- |

| Slide 7 | COURSE MATERIALS Instructor Notes: - Use this slide to review the contents of the Participant Guide. - Review the available handouts. DIRECT: - Direct participants to open their Participant Guide. - Explain the organization of the Participant Guide and its sections. - State that the Participant Guide is for the participants to keep and that they may write in it to record notes. - Tell participants that they should have their Participant Guide in class each day. They may leave it in the classroom each evening. - Review the handouts with participants. |
| --- | --- |

| Slide 8 | COURSE SCHEDULE Instructor Notes: - Review the course schedule by explaining what will be taught each day throughout the training week. DIRECT: - Refer participants to a more detailed course schedule in their Participant Guide. |
| --- | --- |

| Slide 9 NOTE: Another important ground rule may include active participation, especially during group activities. | GROUND RULES Instructor Notes: SAY: “Now, let’s talk about some ground rules for the course.” - Explain that the instructors have 5 ground rules for the class. Walk them through the list. ASK: “What ground rules can you think of that might be important to include for this class?” - Elicit responses from participants. Ensure participants agree to the ground rules (can live with them, even if they don’t totally agree.) - Remind participants that ground rules may be changed, per class needs. - Record all the ground rules on a flipchart page titled “Ground Rules.” When completed, post this page in the room. |
| --- | --- |

| Slide 10 | Where’s the Coffee? Instructor Notes: - Provide administrative information including: - Location of restrooms, coffee and vending areas, and lunch options - Emergency evacuation information - Smoking area - Parking |
| --- | --- |

| Slide 11 | Questions Instructor Notes: ASK: “Does anyone have any questions before we move on?” - Answer any participant questions at this point. If an answer cannot be provided for a participant’s question, add it to the Parking Lot. |
| --- | --- |

MODULE 1: INTRODUCTION TO CMS

# Module 1: Introduction to CMS

Module 1 Description:

In Module 1, participants will gain a basic understanding of continuous monitoring systems (CMS), including learning about four different types of CMS. They will learn the reasons why CMS are important, as well as their many uses. Additionally, participants will learn about the inclusion of CMS into Federal regulations. This module will introduce performance specifications (PS) and quality assurance as it relates to continuous emission monitoring systems (CEMS) and the use of CEMS data for enforcement.

Module 1 Learning Objectives:

- Recognize the different types and uses of CMS

- Identify the regulations that contain CMS requirements

- Recognize, in general, what performance specifications are and how they are used

- Recall enforcement aspects of CMS

Module 1 Preparation:

- Write and circle “CMS” in the middle of a flipchart page.

- Prepare two game cards per a group/table for a knowledge check game. Label one card “True” and the second card “False.”

- Title a flip-chart page “Group Experts” for the culminating Module 1 group activity.

Estimated Time: 180 minutes (3 hours)

| Slide 1 | Module 1: Introduction to Continuous Monitoring Systems (CMS) Instructor Notes: - Introduce participants to Module 1: Introduction to Continuous Monitoring Systems (CMS) SAY: “Module 1 is intended as an introduction to continuous monitoring systems. Let’s look more closely at the topics this module will cover.” |
| --- | --- |

| Slide 2 | Module 1 Outline Instructor Notes: - Review the topics covered in the Module 1 outline. |
| --- | --- |

| Slide 3 | Module 1 Learning Objectives Instructor Notes: SAY: “Here are the objectives that you should be able to accomplish after we complete this module.” - Read the Module 1 learning objectives. |
| --- | --- |

| Slide 4 | What are CMS? Instructor Notes: - Before showing this slide’s contents, conduct a brief discussion with participants. ASK: “What are CMS?” - Elicit responses from participants about what they already know about CMS. - Create a word-web with the participants’ responses on the “CMS” flipchart page. - When completed with the discussion, show and read the definition of CMS. - Explain that the definition is from the National Emission Standards for Hazardous Air Pollutants, or NESHAPS, found in 40 CFR, Part 63. |
| --- | --- |

| Slide 5 | Why CMS? Instructor Notes: - Explain why CMS are essential. - Talk about how with continuous data, facilities are better able to track the performance of regulated units. - Also, discuss the CMS requirements found in the General Provisions of Part 60 and Part 63. Remind participants that facilities subject to 40 CFR part 60 or 63 are also subject to the requirements of the General Provisions unless otherwise specified in the applicable subpart. Tell participants that a handout has been included, which can act as a guide to the relevant requirements found in the General Provisions of both Parts 60 and 63. |
| --- | --- |

| Slide 6 | Basis for CMS Programs Instructor Notes: - Explain the reasons why CMS programs are used. DIRECT: - Direct participants to the Resources page in their Participant Guide to view “The Plain English Guide to the Clean Air Act.” Go to: https://www.epa.gov/clean-air-act-overview/plain-english-guide-clean-air-act |
| --- | --- |

| Slide 7 | Basis for CMS Programs (Cont’d) Instructor Notes: - Explain that EPA requires the use of reference methods and CMS as two methods to measure concentrations of pollutants from regulated sources. |
| --- | --- |

| Slide 8 | Reference Methods Instructor Notes: - Explain the disadvantages of using reference methods when compared to having a CMS installed. |
| --- | --- |

| Slide 9 | CMS Instructor Notes: - Explain the advantages of CMS as a facility’s compliance demonstration. IMPORTANT/KEY MESSAGE: - Highlight that a sorbent trap could be considered not in real time. |
| --- | --- |

| Slide 10 | CMS Are Used To… Instructor Notes: - Read the various uses of CMS. |
| --- | --- |

| Slide 11 NOTE: A CERMS is a system that contains a “flow monitor”. | Types of CMS Instructor Notes: - Read the four types of CMS. SAY: “We will be looking at each of these four types in more detail on the slides that follow.” IMPORTANT/KEY MESSAGE: - Highlight that you may find more than one of these on a stack in a CMS. |
| --- | --- |

| Slide 12 | Continuous Opacity Monitoring Systems (COMS) Instructor Notes: SAY: “Let’s discuss COMS or continuous opacity monitoring systems first.” |
| --- | --- |

| Slide 13 NOTE: How much light went out versus how much came back is used to calculate the % opacity value. The percentage of visible light attenuated is defined as the opacity of the emissions. Transparent stack emissions that do not attenuate light will have a transmittance of 100 percent or an opacity of zero percent. | COMS Instructor Notes: - Define COMS referencing the first bullet on the slide. ASK: “Can anyone define opacity?” - Elicit answers from participants and make corrections and clarifications as needed. Definition of opacity: The percentage of light that is attenuated by an optical medium (Op). - Explain how COMS uses light to determine opacity levels referencing bullet 3 on the slide. - Explain single pass COMS and double pass COMS. Single pass COMS have a transmitter and receiver arrangement with the light beam emitted from the transmitter passing across the duct/stack to a receiver. Double pass COMS have a transceiver and reflector arrangement with the light beam emitted from the transceiver passing across the duct/stack to a reflector, which then returns the light to the transceiver. |
| --- | --- |

| Slide 14 | COMS (Cont’d) Instructor Notes: - Use the image to provide a high-level overview of COMS. - Explain that as emissions flow through the stack or duct the installed COMS measures the amount of opacity. |
| --- | --- |

| Slide 15 | Typical Sources with COMS Requirements Instructor Notes: - Explain where COMS are typically used and provide the examples noted on the slide. |
| --- | --- |

| Slide 16 | Continuous Emission Monitoring Systems (CEMS) Instructor Notes: SAY: “Now, let’s discuss CEMS or continuous emission monitoring systems next.” |
| --- | --- |

| Slide 17 NOTE: CEMS are required under some of the EPA regulations as the method of compliance or as an excess emissions monitor. The individual subparts of the EPA rules usually specify the reference methods that are used to determine the accuracy and precision of the CEMS. | CEMS Definition Instructor Notes: - Define CEMS. - Explain that total equipment includes sample extraction and transport hardware, analyzer/measurement method, data recording and processing hardware, and software. |
| --- | --- |

| Slide 18 | CEMS Instructor Notes: - Explain how CEMS measure emissions by extracting a sample of gas. State that CEMS may also measures particulate matter and flowrate. - Explain that the output range must include the full range of expected concentration values in the gas stream including the zero and span values. |
| --- | --- |

| Slide 19 | CEMS Illustrative Example Instructor Notes: - Explain that this CEMS example contains an opacity monitor, gas analyzer, a flow monitor, in addition to a temperature and pressure monitor. This is typical of what you might see in the field. |
| --- | --- |

| Slide 20 | Basic CEMS Components Instructor Notes: - Discuss the sample interface, analyzer/measurement method, and the data acquisition system of the CEMS. - Explain that the data system is usually referred to as the data acquisition system, or DAS. (Also, under Part 75 it is known as the data acquisition and handling system, or DAHS). |
| --- | --- |

| Slide 21 | Major Components of CEMS Instructor Notes: - State the major components of CEMS. - Give participants the following information for each of the images on the slide: - DAS – An example of a typical DAS screen. NOTE: In this picture of the DAS, you can see highlighted in yellow the areas of concern. - A picture of the typical analyzer installed in a CEMS shed. - A sample gas conditioning system installed in the CEMS shed. |
| --- | --- |

| Slide 22 | Cylinders of EPA Certified Gases and CEMS Cabinet Instructor Notes: - Provide information about cylinders of EPA certified gases and CEMS cabinet. |
| --- | --- |

| Slide 23 | CEMS Unit Shelter Instructor Notes: - Provide information about CEMS shelter. |
| --- | --- |

| Slide 24 | Typical Sources with CEMS Requirements Instructor Notes: - State the examples of some typical stationary sources containing CEMS. |
| --- | --- |

| Slide 25 | Predictive Emission Monitoring Systems (PEMS) Instructor Notes: SAY: “Now, let’s discuss PEMS or predictive emission monitoring systems.” |
| --- | --- |

| Slide 26 | PEMS Instructor Notes: - Define PEMS. |
| --- | --- |

| Slide 27 | PEMS (Cont’d) Instructor Notes: - Explain how PEMS works as a software-based system, and state examples of its input variables. |
| --- | --- |

| Slide 28 | Continuous Emission Rate Monitoring Systems (CERMS) Instructor Notes: SAY: “Now, let’s briefly touch on CERMS or continuous emission rate monitoring systems.” |
| --- | --- |

| Slide 29 NOTE: The flow monitor is usually accompanied by one or more gas monitors (e.g., SO2 or NOx). Both the flow monitor and the gas monitors are needed to determine the pollutant mass emission flow rate. | CERMS Instructor Notes: - Define CERMS. |
| --- | --- |

| Slide 30 NOTE: The following additional regulations may also require the use of CMS, but they usually refer to the QA/QC requirements in the Part 60 (New Source Performance Standards (NSPS) and Part 75 (Acid Rain program) - 40 CFR, Part 63- National Emission Standards for Hazardous Air Pollutants (NESHAPS). Many subparts require the use of CMS and reference the Performance Specifications and Quality Assurance in 40 CFR, Part 60. - 40CFR264/266- Rules for Hazardous Waste | CMS in Federal Regulations Instructor Notes: SAY: “Continuous monitoring systems are usually required by regulations (Federal, State or Local). We’ll now discuss the Federal regulations.” |
| --- | --- |

| Slide 31 NOTE: This is only for NSPS and not for ones under the Acid Rain Program. As these monitors would be under Appendices A and B of Part 75. | 40 CFR, Part 60 - New Source Performance Standards (NSPS) Instructor Notes: - Discuss 40 CFR, Part 60. |
| --- | --- |

| Slide 32 | 40 CFR Part 61 - National Emission Standards for Hazardous Air Pollutants Instructor Notes: - Discuss 40 CFR, Part 61. |
| --- | --- |

| Slide 33 NOTE: Additionally, 40 CFR part 264/266 – Hazardous Waste Facilities: - Part 264 – Standards for owners and operators of hazardous waste treatment, storage, and disposal facilities - Part 266 – Standards for the management of specific hazardous wastes and specific types of hazardous waste management facilities Establish minimum national standards which define the acceptable management of hazardous waste. Many subparts require the use of CMS and reference the Performance Specifications and Quality Assurance in 40 CFR, Part 60. | 40 CFR, Part 63 - National Emission Standards for Hazardous Air Pollutants (NESHAP) for Source Categories Instructor Notes: - Discuss 40 CFR, Part 63. |
| --- | --- |

| Slide 34 NOTE: Some NSPSs (such as 40 CFR, Part 60, Subpart GG and KKKK) may allow the monitoring under 40 CFR, Part 75 to be used instead of the monitoring prescribed in 40 CFR, Part 60. These are usually sources that are already subject to Part 75, or the Acid Rain Program. | 40 CFR, Part 75 – Acid Rain Program Instructor Notes: - Discuss 40 CFR, Part 75. |
| --- | --- |

| Slide 35 NOTE: Quality assurance is basically what is done to make sure that the quality control is working | Performance Specifications and Quality Assurance Instructor Notes: - Define PS and quality assurance. SAY: “Module 3 will provide much more detail about performance specifications and quality assurance.” |
| --- | --- |

| Slide 36 | Use of CEMS Data for Enforcement Instructor Notes: - Describe how CEMS data is used for enforcement. |
| --- | --- |

| Slide 37 | Use of CEMS Data for Enforcement (Cont’d) Instructor Notes: - Continue discussion about CEMS data used for enforcement. |
| --- | --- |

| Slide 38 | Enforcement Applications of CEMS Instructor Notes: - Describe how CEMS data is used for enforcement. SAY: “The next slides will walk you through these two enforcement applications (e.g., 40 CFR, Part 60).” |
| --- | --- |

| Slide 39 | CEMS is the Compliance Method Instructor Notes: - Discuss when CEMS is the compliance method. - Provide the following example: A NSPS which requires CEMS as the Compliance Method is NSPS Subpart D for New Electric Steam Generators. Because CEMS is the compliance method, we can rely on CEMs data alone to prove a violation of the emissions standard in civil litigation. |
| --- | --- |

| Slide 40 | CEMS is not the Compliance Method Instructor Notes: - Discuss when CEMS is not the compliance method. - Provide the following example: CEMs data may be used to issue a Notice or Finding of Violation or for negotiation in cases. We also expect that CEMS data represent emissions comparable to the Compliance Method data. For example, to determine magnitude and duration of emissions violations. Regarding the “General Duty Clause,” Section 60.11(d) establishes a requirement for “good air pollution control practice for minimizing emissions.” CEMs data may be used to ensure compliance with this requirement. |
| --- | --- |

| Slide 41 OPTIONAL KNOWELDGE CHECK ACTIVITY Conduct the knowledge check questions as a whole group eliciting answers from participants in the class. | Let’s Test Your Knowledge! Instructor Notes: SAY: “Now, let’s test your knowledge of Module 1 by participating in a game. This game is called “True or False.” ACTIVITY - Divide participants into small groups. - Distribute two game cards per group/table. One card should be labeled “True” and the second card “False.” - Provide an incentive to the group(s) who gets the most correct (e.g., dismissed for lunch 5 minutes early today/tomorrow). - Explain the directions to the participants. - Instructors will present the first true/false knowledge check on the screen, groups quietly discuss their answer, and the instructor will indicate when all groups should raise their cards. - The instructor will record a point for each question that a group(s) answers correctly. This game format continues for all the knowledge check questions. - Proceed to the following six slides to conduct the activity. |
| --- | --- |

| Slide 42 | Types of Continuous Monitoring Systems Instructor Notes: - True or False? CMS are used to identify periods of excess emissions, assess control equipment efficiency, and monitor control equipment operation. Answer: True! In addition, CMS are also used to: - Demonstrate Compliance with Regulations - Generate Data that can be Used to Develop Regulations - Improve Emission Data Bases - Monitor Process Operating Parameters - Validate Emission Credits - Provide Public Assurance of Compliance |
| --- | --- |

| Slide 43 | Uses of CMS Instructor Notes: - True or False? CEMS are used for continuous compliance determinations or determination of exceedances of the standards. Answer: True! CEMS are used for continuous compliance determinations or determination of exceedances of the standards. - True or False? COMS use light to determine percent opacity. Answer: That true! COMS use light to determine percent opacity - True or False? PEMS use direct measurements of emissions to determine results. Answer: This is false. PEMS use process or control device operating parameter measurements and a conversion equation, graph, or computer program to yield final results. - True or False? CERMS determine and record the pollutant mass emission rate. Answer: It’s true. CERMS are the total equipment required for determining and recording the pollutant mass emission rate (in terms of mass per unit of time). |
| --- | --- |

| Slide 44 | Regulations Instructor Notes: - True or False? The regulations that detail the monitoring, recordkeeping, and reporting requirements of the first national cap and trade program in the US are found in 40 CFR, Part 75- Acid Rain Continuous Emission Monitoring. Answer: This is true. |
| --- | --- |

| Slide 45 | Regulations (Cont’d) Instructor Notes: - True or False? Performance Specifications and Quality Assurance Procedures for CMS are contained in the Appendices of 40 CFR Part 60 – New Source Performance Standards. Answer: That’s true. Performance Specifications and Quality Assurance Procedures for CMS are contained in Appendices B and F, respectively, of 40 CFR, Part 60 – New Source Performance Standards. |
| --- | --- |

| Slide 46 | Performance Specifications Instructor Notes: - True or False? Performance Specifications are used to evaluate the effectiveness of quality control and the quality of data produced by any CEMS. Answer: This is false. Performance Specifications are used for evaluating the acceptability of the CMS at the time of, or soon after installation, or whenever specified in the regulations. The QA procedures are used to evaluate the effectiveness of quality control and the quality of data produced by any CMS. |
| --- | --- |

| Slide 47 Purpose: To become an “expert” on the knowledge learned from Module 1 for an assigned CMS. Share information and help your peers understand and retain this information. Estimated Time: 40 minutes - 20 minutes in groups - 20 minutes in group debrief Preparation Checklist: - Title a flip-chart page “Group Experts” and post in the front of the room. NOTE: While groups are presenting, instructors are encouraged to walk around and observe. | Optional Activity Instructor Notes: OPTIONAL ACTIVITY – SMALL GROUPS - Conduct a Module 1 culminating group activity with participants called “Group Experts.” - Divide the class into four groups: COMS, CEMS, PEMS, and CERMS. - Within each group, participants should discuss what was learned for their assigned CMS. They should practice explaining what it is, how it generally works, and be able contribute 2-3 important facts about it. They should write their facts on post-it notes. - After groups have finished reviewing and learning their assigned CMS, assign groups so that there is one COMS, CEMS, PEMS, and CERMS member per group. - Direct each member of the group (COMS, CEMS, PEMS, and CERMS) to present their knowledge of their assigned CMS to the other members of the group. Encourage each member to present for no more than 5 minutes. - If there are odd numbers and a group is missing a member, instructors can fill in or allow them to listen to another group’s presentation. - Encourage groups to post their facts on the flipchart at the front of the class. - Proceed to the Activity Debrief on the next slide. |
| --- | --- |

| Slide 48 | Activity Debrief Instructor Notes: - Point out some of the important facts that are posted on the flipchart. - Pose the following questions to participants to discuss their learning experience during this exercise. ASK: - “What things did you learn during or after this exercise?” - “What did you find helpful during this exercise?” - “What challenges did you face?” - “Did you learn anything new? If so, what?” |
| --- | --- |

| Slide 49 | Module 1 Summary Instructor Notes: - To wrap-up Module 1, review the learning objectives. |
| --- | --- |