## Slide 1: Module 2: Overview of CMS and CMS Design and Components

## Slide 2: Module 2 Outline

## Slide 3: Module 2 Learning Objectives
At the end of Module 2, learners will be able to:
  Define opacity and describe how continuous opacity monitoring systems (COMS) are used
  Recognize the pollutant parameters measured by continuous monitoring systems (CMS)
  Distinguish between extractive and in-situ systems
  Describe how continuous emission rate monitoring systems (CERMS) function
  Give examples of CEMS location and siting considerations

## Slide 4: Types of CMS
Reminder: There are four main types of CMS. These are:
This module will provide an overview of CEMS, COMS and CERMS. PEMS will be covered later in Module 3, when we discuss Performance Specification 16.

## Slide 5: Pollutant Parameters
Continuous Monitoring Systems (CMS) may be used to measure the following:
  Opacity
  Sulfur Dioxide
  Nitrogen Oxides
  Carbon Dioxide
  Oxygen
  Carbon Monoxide
  Total Reduced Sulfur
  Stack Flow Rate
Hydrogen Sulfide
Volatile Organic Compounds
Particulate matter
Ammonia
Mercury
Hydrogen Chloride
(And other pollutants)

## Slide 6: General Categories of CMS

## Slide 7: Opacity and COMS
7

## Slide 8: Opacity – Setting the Stage
OPACITY (Op)  The percentage of light that is attenuated by an optical medium – in our case, the effluent gas stream.
TRANSMITTANCE (Tr) The percentage of light that is transmitted through an optical medium.
Therefore, Op = 100 - Tr
8

## Slide 9: Transmittance vs. Opacity

## Slide 10: Opacity
Light is reduced by scattering and absorption by the particles in the stack gas exhaust stream.
Amount of light reduction is dependent on type, size, and size distribution of particles.
% opacity is a function of the amount of particulate in the gas stream.
However, the % opacity cannot, in general, be easily correlated to a specific mass emission rate of PM.

## Slide 11: COMS
Single Pass
Double Pass
Can be single pass or double pass design (double pass transmissometer).
Most COMS used for compliance determinations are double pass, which use a light path that is twice the stack diameter.
Require a means to calibrate and periodically (usually quarterly) audit the COMS.
Most have a remote display and control panel in the facility control room or CEMS shelter.
Must have a means to capture, average, and store data measured by the COMS.
Must have means (most use air blowers) to keep stack gas from impinging on and potentially damaging the lenses of the COMS.

## Slide 12: CEMS Design
12

## Slide 13: Basics of CEMS Design
CEMS can be divided into two general categories based on the means by which the sample gas is acquired (captured) and delivered to the analyzer:
1. Extractive systems
Withdraw flue gas from the stack and transport the gas to analyzers.
An extractive system may be either source-level or dilution.
2. In-situ systems
Have at least some part of their analysis subsystem mounted in the stack in direct contact with the flue gas.

## Slide 14: General Extractive System – Conditioning Cabinet

## Slide 15: General Extractive System Components
Probe
Particulate Filter
Sample Conditioning or Dilution
Sample Line
Pump
Controller
Analyzer
Data Calculation and Storage

## Slide 16: Source-Level Extractive System

## Slide 17: Dilution Extractive Systems

## Slide 18: Dilution Extractive Systems (Cont’d)
The sample gas is diluted with dry, contamination-free air to a level below the dew point of the diluted sample gas to eliminate condensation in the sample line.
The diluted sample is measured by pollutant and CO2 monitors operating at or near ambient concentration ranges to provide concentration measurements on a wet basis.
The concentrations are measured on a wet-basis. With a wet stack volume flowrate measurement, the pollutant mass emission rate can be calculated without a separate stack gas moisture measurement or assumption needed.
The most unique component of a dilution-extractive system is the dilution sampling probe.
There are two types, depending on where the dilution occurs:
  In-stack
  Out of stack

## Slide 19: Dilution Probe

## Slide 20: Dilution Probe Orifice

## Slide 21: Reasons to Consider Using Dilution Probes
Allows the emissions to be measured on a “wet” basis
Sampling rate of stack gas (~20-50 mL/min) much lower than conventional extractive systems (~2-5 L/min.) resulting in less PM being pulled in with sample
Reduces moisture of the sample gas, thus not requiring gas conditioning system or “heated” sample lines to prevent condensation to analyzer, which results in lower maintenance
Allows the use of ambient monitors which meet design and performance criteria set by EPA

## Slide 22: Overview of Measurement Bias
Bias is the amount of systematic error of a measurement system
  Consistent in direction (positive or negative) and magnitude
  Different than a random error
Random Error
Systematic Error

## Slide 23: General Sources of Bias for Extractive Systems

## Slide 24: Sources of Biases in Dilution Probes
  If installed after wet scrubbers, moisture or aerosols can enter the probe and change the dynamics of dilution, unless the stack gas is adequately filtered, or the probe is sufficiently sloped (one or two degrees downward) to prevent their entrance.
  Dilution probes are affected by changes in stack gas temperature (Ts), pressure (Ps), and molecular weight (MW), which changes dilution ratio.
  Dilution ratio of a stack gas can change if the MW of the analyzer calibration gas (i.e., “gas blends” vs. “single” gases, and the effect of heavier in a blended gas) is different from the MW of the stack gas.
  Contaminated source “dilution air” can affect dilution ratio or change the measured concentration of the pollutant in the stack gas, either high or low ratio.

## Slide 25: Considerations for Extractive System Components
Filters
  Coarse/Fine
  Quality
Pumps
  Capacity
  Type
  Quality
Cabinets or Shelters
  Location
  Temperature Stability
System Controller
  Microprocessor To Sequence/Control Automatic Functions
Electrical Support
  Fuses
  Circuit Breakers
Calibration Gases
  Location
  Injection Point
  Gas Certification

## Slide 26: In-Situ Systems
Perform analysis at the stack
  Lack of conditioning and transport sub-systems, hence, generally less equipment required than extractive systems
EPA distinguishes between point and path monitors by the amount of gas stream that the probe is blocking.
  Usually “very small” segment (point), or 1 or 2 diameters (path).
There are two types of in-situ systems:
  Point systems – monitor at a single point or along a very short path within the stack.
  Path systems (also called “cross stack”) – monitor across a certain path of stack gas.

## Slide 27: In-Situ Monitors
Cross-Stack (path)
In-Stack (point)
Single Pass
Double Pass

## Slide 28: Advantages of Extractive Systems
Analyzers can be installed in an accessible, clean environment
Ease of maintenance
Time sharing capability
Allows widest selection of analyzer technologies
Can combine more than one analyzer
Can remove interfering substances before measurement
Gas is measured on a dry or wet basis depending on design

## Slide 29: Disadvantages of Extractive Systems
Sample transport and conditioning system is expensive to install and operate and has high power requirements, and has potential for pluggage, leaks and condensation problems (both water and acid)
Sample gas conditioning or dilution is required
May alter sample, may inadvertently remove substances of interest from sample gas
Response time of the sampling system may be slow
Has lots of components and a complicated design
Analyzer may have time-lag with high concentrations

## Slide 30: Advantages of In-Situ Systems
Advantages
Fast response time
No sample transport or conditioning
Simple, less expensive installation
Less equipment to buy and maintain
Has few components
Disadvantages
Vibration sensitive
Access for service and maintenance can be difficult
Limits choice of analyzer
Does not allow for expansion
Operates in a potentially harsh environment
Path type may not be able to be located downstream of sorbent injection or spray dryer systems

## Slide 31: Disadvantages of In-Situ Systems
Advantages
Fast response time
No sample transport or conditioning
Simple, less expensive installation
Less equipment to buy and maintain
Has few components
Disadvantages
Vibration sensitive
Access for service and maintenance can be difficult
Limits choice of analyzer
Does not allow for expansion
Operates in a potentially harsh environment
Path type may not be able to be located downstream of sorbent injection or spray dryer systems

## Slide 32: CEMS Components
32

## Slide 33: External Probe Filters

## Slide 34: Filter Blow Back

## Slide 35: Internal Coarse Filter
Probe
Heated line
Sintered filter
Calibration gas
Sample gas

## Slide 36: Inertial Filter
Filtered sample
Filtered sample gas (.005 ft/s)
Unfiltered sample (100 ft/s)
Radial flow

## Slide 37: Example of How a Dilution Probe Works

## Slide 38: 1. Let’s Test Your Knowledge!
38

## Slide 39: CEMS Design – Question 1
1. __________ systems condition the sample gas before analysis.
A. In-situ
B. Opacity
C. Dilution Extractive
D. Source Level Extractive
The answer is D. Source Level Extractive
39

## Slide 40: CEMS Design – Question 2
2. In-situ CEMS require __________ equipment for a single sample point compared to extractive CEMS.
A. More
B. Less
C. The same amount of
The answer is B. Less.
40

## Slide 41: CEMS Design – Question 3
3. Transmittance is the percentage of light that is attenuated by an optical medium.
True
False
It’s false. Actually, opacity is the percentage of light that is attenuated by an optical medium. In our case, the effluent gas stream. Whereas, transmittance is the percentage of light that is transmitted through an optical medium.
41

## Slide 42: CEMS that Include a Flow Monitor (Continuous Emission Rate Monitoring Systems or CERMS)
42

## Slide 43: Continuous Emission Rate Monitoring Systems (CERMS)
CERMS are:
  Used in conjunction with gas concentration measurements, to calculate mass emission rates.
  Required for most sources subject to 40 CFR Part 75.
Pollutant Mass Emission Rate (PMER) = CS AS VS
  CS = Concentration
  AS = Stack Area
  VS = Stack Gas Velocity
  lbs/hr = (lb/ft3) (ft2) (ft/hr)

## Slide 44: Differential Pressure Measuring

## Slide 45: Ultrasonic Flowmeter
An ultrasonic flowmeter uses a pair of transmitter/receivers mounted on opposite sides of the stack, with one upstream from the other. The signal is alternated between them, sending it in the direction of stack gas flow, where it is speeded up, and then against the direction of flow, where it is slowed down. The difference in the time between the two signals is proportional to the stack gas velocity.
Acoustic Velocity

## Slide 46: Considerations When Choosing a Location for CEMS
For specific requirements, see applicable performance specification.
Representative Emissions (well-mixed and laminar flow)
Accessibility for routine maintenance and repairs and performance of calibration audits and checks
Sufficient distance from flow disturbances, such as bends from changes in stack/duct diameter, and control equipment
Protection from weather and vibration
For opacity monitoring systems: no condensation inside stack near monitor and no ambient light

## Slide 47: Access for Reference Method Testing

## Slide 48: 2. Let’s Test Your Knowledge!
48

## Slide 49: CERMS – Question 1
1. For CERMs, the calculation of pollutant mass rate requires velocity measurements.
True
False
It’s true! For CERMs, the calculation of pollutant mass rate requires velocity measurements.
49

## Slide 50: CERMS – Question 2
2. A CERMS is used when which of the following is required:
A. The gas concentration
B. The mass emission rate
C. Both
The answer is B. A CERMS is needed to calculate the mass emission rate
50

## Slide 51: CEMS
1. Important factor(s) for installation of CEMS is/are:
A. Accessibility
B. Representativeness
C. Sufficient distance from flow disturbances
D. Protection from weather and vibration
E. All of the above
The answer is E, All of the above. All the factors are important for installation of CEMS.
51

## Slide 52: Activity
Title: Top Ten
Purpose: To review the module content by sharing a list of top ten things learned about CMS and its design and components.
Time: 40 minutes
            20 minutes in groups
            20 minutes group debrief
52

## Slide 53: Activity Debrief
53

## Slide 54: Module 2 Summary
Now that you have completed Module 2, you should be able to:
  Define opacity and describe how continuous opacity monitoring systems (COMS) are used
  Recognize the pollutant parameters measured by continuous monitoring systems (CMS)
  Distinguish between extractive and in-situ systems
  Describe how continuous emission rate monitoring systems (CERMS) function
  Give examples of CEMS location and siting considerations