## Slide 1: Incinerators (TOXC222)

## Slide 5: Incineration
“A combustion process, in which the primary purpose is to destroy combustible material.”
Biomedical Incinerators: Hospital, Pathological and Crematory Incinerators.
Heat Stripping Ovens (Burn off ovens)
MSW incinerators
Sewage Sludge incinerators
Hazardous Waste incinerators
Commercial and Industrial Incinerators
Air Curtain Incinerators

## Slide 6: Combustion Efficiency
3 Ts
Time
Temperature
Turbulence

## Slide 7: Combustion
Stoichiometric combustion
Excess air combustion
Sub-stoichiometric combustion

## Slide 8: IIA Waste Classification
Varies By:
  Composition
  Moisture content
  BTU value per pound fired
TYPES 0 - 8

## Slide 9: Solid Waste Incinerators
Open Burning
Open-Pit Incinerators
Teepee Burners
Single Chamber Incinerators
Multiple Chamber Incinerators
Controlled Air Incinerators
Rotary Kiln Incinerators
Fluidized Bed Incinerators
Multiple Hearth Incinerators
Air Curtain Incinerators

## Slide 10
Single Chamber Incinerator
Ash
Removal
Door
Underfire
Air Ports
Auxiliary
Fuel
Charge Door
Overfire
Air
Ports
Stack
Combustion
Chamber
Refractory
Waste
Grate
Ash Pit

## Slide 12
Controlled-Air Incinerator with Staged Hearth and Automatic Ash Removal
Secondary Burner
Primary Burner
Ash
Sump
Ash Quench
Ash Chute
Ash Discharge Ram
Ash Transfer Rams
Feed Ram
To Stack or Boiler
Secondary Chamber

## Slide 13
Stages
Rams
Al

## Slide 14
Controlled Air Incinerator Components
Stack
Secondary Chamber
View Port
Secondary Burner
View Port
Ash Removal
Door
Primary
Chamber
Primary Burner
Primary Combustion Air Burner Blower
Mechanical Charge System
Secondary Combustion Air Blower
Control Panel

## Slide 15
Secondary
Primary

## Slide 16
Blower

## Slide 17
AFTERBURNER

## Slide 18
In-line
Multiple-
Chamber
Incinerator
(Excess-Air)
Charging
Door
Ignition Chamber
Secondary
Combustion
Chamber
Curtain Wall
Port
Mixing
Chamber
Curtain
Wall
Flame Port
Secondary
Air Port
Clean
Out
Doors
Cleanout
Doors
Grates
Location of
Secondary
Burner

## Slide 19
Retort
Multiple Chamber
Incinerator
Charging Door
Flame Port
Secondary
Air Ports
Secondary
Burner Port
Mixing
Chamber
First
Underhearth
Port
Hearth
Ignition Chamber
Stack

## Slide 21
Flame Port

## Slide 24
Loading Door
Hearth Air
Jets
Insulating
Block
Cremation Hearth
Castable support Arch
Refractory Lined Floor
Insulating Block
Divider Wall
Insulated
Firebrick
Rear Wall
Insulating
Block
Castable
Support Lintel
Throat Air Jets
FRONT
Quickset Insulation
Insulating Block
Cremation Burner
Castable Roof
Insulating Block
Exhaust Gas Outlet
Afterburner
CREMATOR

## Slide 30: Categories of Industrial Incinerators
Volume Reduction (trash, wood, solid waste streams)
Toxicity Reduction (any toxic waste stream)
Resource Recovery (copper wire, steel drums, electric motors)
Energy Recovery

## Slide 31: Industrial Heat Cleaning (Burnout) Ovens
Primary Chamber 700 - 750 F
Secondary Chamber 1200 -1400 F
Roasting Condition in Primary
Low Oxygen Environment
Volatiles & Smoke go to Afterburner
Water Mist Injection in Primary

## Slide 49: Modes of Operation
Waste Charging:
  Batch
  Intermittent
  Continuous
Ash Removal:
  Manual
  Automatic

## Slide 50
Hydraulic Fire
Door Actuator
Waste Charging Hopper
Hopper Cover
Fire Door
Ram Face
Quench Spray
Primary
Combustion
Chamber
Furnace
Opening
Hydraulic
Ram
Actuator
HOPPER-RAM
Charging
Ram

## Slide 56: Typical Incinerator Operating Procedures
Before Start-up
Start-up
Charging/Burning
Burn Down
Shutdown (batch & intermittent)

## Slide 57: Before Incinerator Start-up
Manual Ash Removal
Automatic Ash Removal
Routine Daily Inspection
Burner & Blower Check

## Slide 58: Typical Incinerator Operating Procedures
Operating Step
Typical Duration
1. Ash Cleanout
15 to 30 minutes
2. Pre-Heat
15 to 60 minutes
3. Charging & Burning
Up to 14 hours
4. Burndown
2 to 4 hours
5. Cooldown
5 to 8 hours

## Slide 59: Incinerator Operation
Waste Logging
Pre- Heating
Charging

## Slide 60: Shutdown
Batch or Intermittent Duty:
  Combustion Blowers left on to cool
  Typically lasts 5 to 8 hours
  Ash removed and inspected

## Slide 61: Typical Operational Errors
Charging before Operating Temps. Are Achieved (failure to Pre-heat)
Overcharging
Waste with Excessive Moisture

## Slide 62: Incinerator Emissions & Control

## Slide 63: Emissions
Visible Emissions (Stack or Fugitive)
Particulate Matter (Concentration/Weight)
Acid Gases (NOx, SOx, HCl)
Toxics (Dioxins, Furans, Heavy Metals)

## Slide 64: Pollutant Formation Factors
Fuel Composition
Charging Method and Rate
Incinerator Type and Design
Combustion Conditions (3 T's)
Excess Air

## Slide 65: Incinerator Emissions Control
Source Separation
Combustion Control
Flue Gas Controls
  (APC equipment)

## Slide 66: Particulate Matter Formation
Suspension of Inorganic Substances
Incomplete Combustion of Fuel Materials
Condensation of Vaporous Metals

## Slide 67: Smoke Formation
Black Smoke
  Too Little Oxygen Relative to Fuel
  Usually Caused by Overcharging
White Smoke
  Premature Cooling of Flue Gas
  Excessive Air
  Inorganic Particles

## Slide 68
"POSITIVE" CONDITION - SMOKE LEAKING
Too Much
Highly Volatile
Waste
Malfunction in Stack
Damper or Fan
Too Much Underfire Primary Air
Adjust Ash
Ram Discharge
Cycle
Burner
Overfired
Temp. Too High

## Slide 69
Too Much
Highly Volatile
Waste
Not Enough
Secondary Air
Too Much Underfire Air
Poor Mixing
Burner Failure,
Temperature too Low
BLACK SMOKE
(Incomplete Burning - Soot Formation)

## Slide 70
WHITE/BLUE SMOKE
Secondary
Chamber
Temperature
Too Low
Too Much
Secondary Air
Too Much
Underfire Air
Problem Waste
Material

## Slide 71
Visible Fly Ash
Flame Port Air
Air Infiltration
Excessive Underfire Air
Problem Wastes
High Primary
Temperature
High Draft Too High

## Slide 72: Carbon Monoxide Formation
Insufficient Oxygen for Complete Combustion
Indicator of Inadequate Combustion Air Turbulence
Indicator of Combustion Efficiency

## Slide 73: Products of Incomplete Combustion (PIC’s)
Greater Combustion Efficiency = Lower Dioxins
Can occur when charging PVC plastics
Dioxins are some of the most toxic man-made substances
Polycyclic Aromatic Hydrocarbons (PAH’s)
Polychlorinated Biphenyls (PCB’s)

## Slide 74: Wet Scrubbers
Remove both Particulates & Acid Gases
Rely on Flue Gas Pressure Drop for Particulate Removal with Alkali Reagent for Acid Gas Removal.
Categories of scrubbers:
  Spray Chambers
  Packed Towers (Beds)
  Venturi

## Slide 75: Wet Scrubber Acid Gas Removal
Sodium Hydroxide (NaOH - Caustic Soda) or Sodium Carbonate (Na2CO3)
Alkali Added to Re-circulation Tank Water (pH of 8-9).

## Slide 76
Liquid
Sprays
Clean Exhaust Gas
Water
Drain
Dirty Flue Gas
Spray Tower,
Countercurrent-Flow
Type

## Slide 77
Spray Tower
Filtration &
Pumps
Blower
Motor

## Slide 78: Common Spray Tower Scrubber Problems
Liquor Spray Nozzles Plugged
Erosion of Spray Nozzles
Corrosion of Shell
Mist Re-entrainment
pH too low or high

## Slide 79
Countercurrent- Flow Packed-Bed Scrubber
Dirty Exhaust
Clean Exhaust
Shell
Mist Eliminator
Liquid Sprays
Packing

## Slide 80
PACKED BED
SCRUBBER
Exhaust
Gas Inlet
Liquor
inlet

## Slide 81: Packed-Bed Operating Problems
Accumulation of Solids
Settling of Packing Material
Liquor pH (between 5.5-10)

## Slide 82
SPRAY VENTURI WITH RECTANGULAR THROAT
Liquid Inlet

## Slide 83
Particle Behavior in Venturi-Scrubber Section
Particles Accelerate
Converging Region
Particles collide with droplets
Droplets have no axial velocity
Particles Decelerate
Droplets Accelerate
Diverging Region
Spray Nozzle
Throat
Flue-Gas Outlet to Separator Tower Section
Flue-Gas Inlet
from Quench

## Slide 84
Liquor Flow
Exhaust Gas Flow
Notes: FLUE GAS STREAM

## Slide 85: Dry Scrubber / Baghouse

## Slide 87: Electrostatic Precipitator

## Slide 91
Notes: FLUE GAS STREAM

## Slide 92
AP Controls for Sewage Sludge Incinerator (video)
Notes: FLUE GAS STREAM

## Slide 98
Putting it all together (video)

## Slide 99: Regulations

## Slide 100: State and Local Regulatory Requirements
General Air Emissions Limitations
  Visible Emissions
  Particulate Matter
  Fugitive Dust
  Gaseous Emissions
  Toxic Emissions
Public Nuisance (Odors, Noise)

## Slide 101: State and Local Agency Incinerator Rules
Crematories
  Human
  Animal
Burn Off Ovens
Pathological waste, low-level radioactive waste, and/or chemotherapeutic waste
Acceptable Incinerators
Regulations more stringent than Federal Regs

## Slide 102: Federal Incinerator Rules
Large Municipal Waste Combustors
Small Municipal Waste Combustors
Other Solid Waste Incinerators
Hospital, Medical, Infectious Waste Incinerators
Sewage Sludge Incinerators
Commercial Industrial Solid Waste Incinerators
Hazardous Waste Incinerators

## Slide 103: Large Municipal Waste Combustors
40 CFR 60 Subpart E - Construct after 8/17/71
40 CFR 60 Subpart Ea – Construct 12/20/89 to 9/20/94
40 CFR Subpart Eb - Construct after 9/20/94, Mod or Recon after 6/19/96
40 CFR 60 Subpart Cb – EG - Existing on or before 9/20/94
40 CFR 62 Subpart FFF – FP - Existing on or before 9/20/94
Notes: 5

## Slide 104: Subpart Eb
> 250 tpd MSW
Siting requirements and Materials separation plan
Operator training and certification
Emission limits for PM, Cd, Pb, Hg, SO2, HCl, Dioxin/Furan, NOx, CO, Opacity, Fugitive ash
CEMs – O2 or CO2, COM, SO2, NOx, CO
Initial testing for all contaminants with limits
Annual testing for PM, Hg, Cd, Pb, HCl, D/F (or CEMS)
Monitoring, recordkeeping and reporting
Limits for air curtain incinerators burning yard waste
Notes: 5

## Slide 105: Small Municipal Waste Combustors
40 CFR 60 Subpart AAAA - Construct after 8/30/99, Mod or Recon after 6/6/01
40 CFR 60 Subpart BBBB – EG - Existing on or before 8/30/99
40 CFR 62 Subpart JJJ – FP - Existing on or before 8/30/99
Notes: 5

## Slide 106: Subpart AAAA
35-250 tpd MSW
Siting requirements and Materials separation plan
Operator training and certification
Good combustion practices
Emission limits for PM, Cd, Pb, Hg, SO2, HCl, Dioxin/Furan, NOx, CO, Opacity, Fugitive ash
CEMs – O2 or CO2, COM, SO2, CO, NOx for Class 1
Initial and Annual testing for PM, Hg, Cd, Pb, HCl, D/F
Class 2 may have less annual testing
Monitoring, recordkeeping and reporting
Limits for air curtain incinerators burning yard waste
Notes: 5

## Slide 107: Other Solid Waste Incinerators
40 CFR 60 Subpart EEEE - Construct after 12/9/04, Mod or Recon after 6/16/06
40 CFR 60 Subpart FFFF – EG - Existing on or before 12/9/04
Notes: 5

## Slide 108: Subpart EEEE
<35 tpd MSW and Institutional units
Siting requirements and waste management plan
Operator training and qualification
Good combustion practices
Emission limits for PM, Cd, Pb, Hg, SO2, HCl, Dioxin/Furan, NOx, CO, Opacity
CEMs – O2, CO
Initial and Annual testing for all pollutants
Less frequent than annual testing may be allowed
Monitoring, recordkeeping and reporting
Limits for air curtain incinerators
Notes: 5

## Slide 109: Hospital, Medical, & Infectious Waste Incinerators
40 CFR 60 Subpart Ec - Construct after 6/20/96 to 12/1/08, Mod after 3/16/98 to 4/6/10, Construct after 12/1/08, Mod after 4/6/10
40 CFR 60 Subpart Ce – EG – Construct on or before 6/20/96, Mod on or before 3/16/98, Construct after 6/20/96 to 12/1/08, Mod after 3/16/98 to 4/6/10
40 CFR 62 HHH - FP
Hospital, Medical, & Infectious Waste Incinerators
Notes: 5

## Slide 110: Subpart Ec
Siting requirements and waste management plan
Operator training and qualification
Emission limits for PM, Cd, Pb, Hg, SO2, HCl, Dioxin/Furan, NOx, CO, Opacity, Fugitive ash
Various emission limits for different dates and size of units
CEMs – CO
Initial and Annual testing for all pollutants ( or CEMs)
Monitoring, recordkeeping and reporting
Notes: 5

## Slide 111: Sewage Sludge Incinerators
40 CFR 60 Subpart O - Construct after 6/11/73
40 CFR 60 Subpart LLLL – Construct after 10/14/10, Mod after 9/21/11
40 CFR 60 Subpart MMMM – EG – Construct before 10/14/10
40 CFR 62 LLL – FP - Construct before 10/14/10
Notes: 5

## Slide 112: Subpart LLLL
Siting requirements
Operator training and qualification
Emission limits for PM, Cd, Pb, Hg, SO2, HCl, Dioxin/Furan, NOx, CO, Fugitive ash
Various emission limits for different dates and size of units
CEMs – CO
Initial and Annual testing for all pollutants ( or CEMs)
Monitoring, recordkeeping and reporting
Notes: 5

## Slide 113: Commercial & Industrial Solid Waste Incinerators
40 CFR 60 Subpart CCCC - Construct after 6/4/10, Mod or Recon after 8/7/13
40 CFR 60 Subpart DDDD – EG – Construct on or before 11/30/99 and not modified or reconstructed after 6/1/01, Construct after 11/30/99 but no later than 6/4/10 or commenced modification or reconstruction after 6/1/01 but no later than 8/7/13, Construct on or before 6/4/10 or commenced modification or reconstruction after 6/4/10 but no later than 8/7/13
40 CFR 62 III – FP - Construct before 11/30/99
Notes: 5

## Slide 114: Subpart CCCC
Incinerate solid waste as defined in 40 CFR Part 241
Siting requirements and Waste management plan
Operator training and qualification
Emission limits for PM, Cd, Pb, Hg, SO2, HCl, Dioxin/Furan, NOx, CO, Fugitive ash
Various emission limits based on dates of construction, mod or recon and type of unit
CEMs – required based on unit type, other monitors required based on APC type
Initial and Annual testing for all pollutants (or CEMs)
Monitoring, recordkeeping and reporting
Air curtain incinerator requirements
Notes: 5

## Slide 115: Hazardous Waste Incinerators
40 CFR 63 Subpart EEE
Notes: 5

## Slide 116: Subpart EEE
HWI, Cement kilns, Lightweight Aggregate kilns, some boilers
Operator training and qualification
Emission limits for PM, Cd, Pb, Hg, HCl, Dioxin/Furan, CO, As, Be, Cr, hydrocarbons, Cl gas
DRE 99.99%. But 99.9999% for dioxin listed hazardous waste
CEMs – Hydrocarbon, COM, PM
Extensive unit performance testing
System interlocks (AWFCO) to stop flow of material
Initial and Annual testing for all pollutants
O&M plan
Monitoring, recordkeeping and reporting
Notes: 5

## Slide 117: Incinerator Inspection

## Slide 118: Inspector Safety Equipment
Hard Hat
Safety Glasses or Goggles
Gloves
Steel Tipped Safety Shoes
Ear Protectors
District Safety Policy

## Slide 119: Identify Potential Safety Problems
·
·
·
·
·
·
·
·
·
Eye Injuries:
  Watching flames through hatches
  Scrubber liquor
Sharps & Infectious Wastes:
  Avoid Skin contact
Burns:
  Contact with hot equipment
Inhalation Hazards:
  Fugitive leaks, high pressure scrubbers/ducts
  Alkaline reagent storage/mixing equip Stacks or vents

## Slide 120: Common Safety Problems
·
·
·
·
Weak or Slippery Walkways/Ladders
Corroded Ductwork or Control Devices
High Electrical Voltage, Control Cabinets
Rotating Equipment: Fans/Fan Belts

## Slide 122: Compliance w/Permit Requirements
Temperature (preheat and or operating)
Type of Waste
Charging Rate
Hours of Operation
Monitoring
Recordkeeping
Many Others

## Slide 123: Points of Inspection
Capture
Transport
Air Mover
Instrumentation
Control
Subsystem

## Slide 124: Capture
Are Emissions immediately Drawn into a control Device?
Collection device
  Hoods

## Slide 125: Transport
Are Emissions Moved to the Control Device Without Loss
Are There any Leaks

## Slide 129: Air Mover
Is the fan big enough for the Job?
Is it Operating as Designed and Permitted?

## Slide 130
Horsepower ?

## Slide 132: Instrumentation
Are the proper instruments present?
Do these instruments appear to be functioning?
Are the instruments showing the appropriate units?

## Slide 133
pH Meter
Scrubber Pressure Drop

## Slide 135: Control Device
Is it On?
Visible Emissions?

## Slide 138: Subsystem
What is the Ultimate Fate of the Captured Emissions?

## Slide 140
What about Violations?
Notice To Comply (NTC)
  Minor Deficiency
  Non-Emissions Related
  Non-Recurring

## Slide 141
What about Violations?
Notice Of Violation (NOV)
  Emissions Related
  Same Problem At Last Inspection

## Slide 142
Four Options After A NOV
Continue to Operate in Violation
Cease the Non-compliant Activity (shut down the operation)
Correct the Problem
Apply for a Variance