## Slide 1
Industrial Boilers
Notes: First slide for 35mm show.

## Slide 2: Course Overview
Air Pollution
Boiler Uses
Boiler Theory and Operation
Air Pollution Formation
Air Pollution Control Devices
Boiler Regulations
Typical Permit Conditions
Inspection Procedures
Why
What
How

## Slide 3
NO2
NO
O
O2

## Slide 4
Electrical generation
Space heating
Food preparation
Commercial laundries
Pulp & paper industry
Petroleum industry
Chemical industry
Municipalities : Water, Sewage & Garbage
High Pressure (2,000 -3,800 psi)
Low Pressure (150 – 1,600 psi)
Liquid water
Liquid water and steam
Saturated Steam
Superheated Steam
Uses of Boilers

## Slide 5
Small Firetube Boiler

## Slide 6
Industrial Boiler

## Slide 7
Babcock & Wilcox Utility Boiler

## Slide 8
CO Catalyst
SCR Catalyst
HP Steam Drum
HP Boiler #1
HP Boiler #2
LP Boiler
Deaerator
LP Steam Drum/ DA Storage
HRSG
Boiler

## Slide 9
Boilers & Opacity

## Slide 10
History of Boilers : Ringelmann Chart

## Slide 11: Hot Numbers
British Thermal Unit (BTU)
  1 BTU the amount of energy needed to heat one pound of water one degree Fahrenheit or  energy given off by burning one wooden match
Lower Heating Value (LHV)
  Heating value of a fuel not counting heat needed to vaporize water
Higher Heating Value (HHV)
  Heating value of a fuel including heat needed to vaporize water

## Slide 12
Boiler Ratings =
Millions of BTU/hr
Boiler HP
Pounds of Steam/hr
Megawatts
Tons per day

## Slide 13
Typical Boiler Rating

## Slide 14: Boiler Fuels
Natural gas
Diesel fuel oils
Tire Derived Fuel (TDF)
Coal/Petroleum Coke
Municipal waste
Bio-Mass
Waste gas
Nuclear

## Slide 15: Steam Plant Basic Elements

## Slide 16: Heat Transfer Methods
Notes: Radiant
Section

## Slide 17
Firetube &
Water Tube Boilers

## Slide 18: Fire-Tube Boiler

## Slide 19: Fire-Tube Boiler

## Slide 20
Small Fire-Tube Boiler

## Slide 21
Fire-Tube Boiler

## Slide 22: Water-Tube Boiler

## Slide 23
Water-Tube Boiler

## Slide 24
Graphics Courtesy of ERI
Boiler Construction
Notes: The section of the boiler, where the primary method of heat transfer from the flame to the tubes is radiation :
is often called the furnace, firebox, or radiant section of the boiler
10,000 – 15,000 pph

## Slide 26
Boiler Tubes

## Slide 27
Boiler Tubes with Fins

## Slide 28
Boiler Circulation

## Slide 29
Water to Steam Circulation Loop

## Slide 30
Boilers

## Slide 31
Natural Circulation

## Slide 32
TEG Flow
Forced Circulation

## Slide 33
Boiler
Air Requirements

## Slide 34
Draft
  Natural
  Forced
  Induced
Combustion air
  Primary
  Secondary
  Excess
Boiler Air Requirements

## Slide 35
Forced Draft Fans

## Slide 36
Induced Draft Fan

## Slide 37
Induced Draft Fans

## Slide 38
Gas Fired Water Tube Boiler

## Slide 39
Economizers
& Air-Preheaters

## Slide 40
Economizer – H2O Inside Tubes

## Slide 41
Air Pre-Heater

## Slide 42
Air Pre-Heater : Ambient to 400F +

## Slide 43
Fire Wall

## Slide 44
Refractory Lining
Boiler Tubes

## Slide 45
Boiler Tubes

## Slide 46
Fluidized Bed Boilers

## Slide 47
Fixed
Bed
Minimum
Fluidization
Bubbling
Bed
Circulating
Bed
Start
No Air Flow
Fluidized Bed Modes

## Slide 48
Circulating Fluidized Bed (CFB)

## Slide 49
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 50
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater
1
2
3
4
5
6
7
8
9
10

## Slide 51
Fluidized Bed Distributor Plate & Bubble Caps

## Slide 52
Feed Lot
Enclosed Conveyors

## Slide 53
Fuel Storage Silo
Enclosed Conveyor

## Slide 54
Water to Steam Loop

## Slide 55
Superheater
Economizer
Furnace
Air Preheater

## Slide 56
Pulverized
Coal Lines:
Gravity Fed

## Slide 57
Inside the
Boiler

## Slide 58
Water Tubes

## Slide 59
Water Tubes

## Slide 60
Re-cir.
Fines
Nozzle
????

## Slide 61
Distributor Plates & Bubble Caps

## Slide 62
Bubble Caps

## Slide 63
Bed Nozzles & Underfire Air

## Slide 64
Ash
Loadout

## Slide 65
High Pressure Steam Drums

## Slide 66
Steam Drum w/Cyclone & Chevron Separators

## Slide 67
STEAM OUTLET
CONTINUOUS BLOWDOWN
FEEDWATER INLET
CHEMICAL FEED
FEEDERS
RISERS
VORTEX BREAKER
MESH PAD
STEAM DRUM INTERNALS CYCLONES WITH MESH PAD

## Slide 68
STEAM OUTLET
MESH PAD
RISER
BAFFLE
FEEDER
RISER
CONTINUOUS BLOWDOWN
CHEMICAL FEED
STEAM DRUM INTERNALS BAFFLE PLATE WITH MESH PAD

## Slide 69
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 70
Circulating Fluidized
Bed Boiler
Interactive Exercise
1
2
3
4
5
6
7
8
9
10
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 71
Power
Generation

## Slide 72
High Pressure Steam Lines

## Slide 73
High Pressure
Steam Lines

## Slide 74
Steam Turbine

## Slide 75
Steam Turbine

## Slide 76
Steam Turbine
Generator

## Slide 77
Cooling Towers

## Slide 78
Cooling Tower Shell

## Slide 79
Typical Control Room

## Slide 80
Utility Boiler
Steam
Turbine

## Slide 81
Steam
Turbine
Blades

## Slide 82
Steam Turbine

## Slide 83
HP Steam
Turbine

## Slide 84
Generator
Steam Turbine

## Slide 85
Brush DAX Turbogenerator

## Slide 86
Generator Rotor

## Slide 87
Generator Rotor

## Slide 88
Generator Stator

## Slide 89
Step-Up Transformers

## Slide 90
Boiler
Steam turbine
Generator
Cooling Media
Condenser
Deaerator
Stack
ESP
Induced Draft Fan
Forced Draft Fan
HP Feedwater Heaters
LP Feedwater Heaters
Fuel
Pump
Typical Electric Utility Plant

## Slide 91
Emissions & Controls

## Slide 92
H2O
CO2
CO
NOX
HC
SOX
PM
CHO
Fuel
+
Air
(N2, O2)
Emissions From Boilers

## Slide 93
Boiler Design
Proper Maintenance
Operating Conditions
Fuel Types
Combustion Modifications
Exhaust Treatment
Emissions Control Methods

## Slide 94
Low-NOx burners
OFA
Ammonia injection (SNCR)
Catalysts (SCR)
FGR
FGD
Control of Gaseous Emissions

## Slide 95
Time
Temperature
Turbulence
Oxygen
Nitrogen
Combustion Considerations

## Slide 96
Thermal NOx
Fuel-bound NOx
Prompt NOx
NOx Creation

## Slide 97
Thermal NOx vs. Temperature

## Slide 98
NOx FORMATION
  N + O NO
  N + OH NO + H
NOx REDUCTION
  CH + NO HCN + O2 (Reversible)
  CH2 + NO HCN + OH (Reversible)
  C + NO CN + O2
  NHi + NO N2 + H2O
  THESE NOx REDUCTANTS ARE FORMED BY PARTIAL COMBUSTION IN A REDUCING ATMOSPHERE
  THE INTERMEDIATE SPECIES, HCN & CN, ARE CONVERTED TO N2, CO2 & H2O IN THE FINAL BURNOUT ZONE
COMBUSTION MODIFICATION

## Slide 99
Rapid Formation <1ms.
Little affect from temperature.
Presence of CHi & HCN during initial combustion can contribute to prompt NOx formation in an oxidizing environment but will inhibit NOx formation in a reducing environment.
Presence of C & NHi in initial combustion process reduces the formation of prompt NOx.
Reactor combustion is controlled to a stoichiometry <.6 and a temperature <2400F.
PROMPT NOx

## Slide 100
N2
HCN
+C
CN
NO
+O
NCO
NHi
+CH2
+H
+OH
+H20
HNCO
+NO
+CH3
H2CN
+NHi
NO2
O2, H2O
HOCN
H
PROMPT NOx

## Slide 101
NOx Production vs. Air/Fuel Ratio

## Slide 102
Modern conventional burners
  NOx less than 80 ppm (<0.1 lb/MMBtu)
Low-NOx burners
  NOx less than 30 ppm
  (<0.04 lb/MMBtu)
Ultra Low-NOx burners
  9 ppm NOx
  (<0.01 lb/MMBtu)
Industry Burner Definitions

## Slide 103
Flue Gas Recirculation (FRG)

## Slide 104
Flue Gas Recirculation (FGR)

## Slide 105
Flue Gas Recirculation (FGR)

## Slide 106
Flue Gas Recirculation (FGR)

## Slide 107
FGR

## Slide 108
FEATURES
CAN USE FGR FLOWS AS HIGH AS 40% OF THE TOTAL STACK EFFLUENT
SOME SYSTEMS OPERATE VERY CLOSE TO THE LIMITS OF FLAMABILITY
SOME SYSTEMS OPERATE WITH VERY RAPID MIXING, VERY CLOSE TO STOICHIOMETERY.
CON’S
HIGH ELECTRICAL USAGE (FGR fan HP doubled compared to RX system)
LOW TEMPERATURE, TRANSLUCENT, FLAME REDUCES HEAT TRANSFER & EFFICIENCY.
COMBUSTION INSTABILITY
CAN’T CHANGE FIRING RATE FAST ENOUGH TO FOLLOW CHANGING LOAD DEMANDS
FGR BURNERS

## Slide 109
Simple durable refractory & steel construction results in:
  Lower initial cost
  Lower maintenance costs
Lower operating cost
  Less stack losses due to low excess air and low FGR requirements
  Lower fan costs
  Eliminates the need for chemicals & catalysts
Lower Cost to Industry

## Slide 110: Flame Temperature vs. FGR
Graphic Courtesy of Coen

## Slide 111
FGR Impact

## Slide 112
Staged Combustion

## Slide 113
Gas Pre-Mix Burner

## Slide 114: Low-NOx Burner with Staged Fuel

## Slide 115
Low-NOx Burner with Staged Fuel
Notes: TQ
#12
TQ
#11

## Slide 116
Ultra Low-NOx Burner (9 ppm)

## Slide 119
Burner Cross-Sectional View

## Slide 120
Typical Components
Reactor
Lean Jet
Fuel Valves & Servos

## Slide 121: Typical Components
REACTOR PORT
LEAN JETS

## Slide 122
Rich Flame
Lean Flames (x4)
Burnout Zone
FGR
A Look Down the Furnace

## Slide 123: Staged Combustion w/Overfire Air

## Slide 124
Graphic Courtesy of B&W
Burners w/Overfire Air

## Slide 125
A B C
NOx Reduction by Boiler Configuration
A: Low-NOx burner only, no overfire air (OFA)
B: Low-NOx burner with OFA
C: Low-NOx burner with OFA and FGR

## Slide 126
Cost $/ Ton NOx Removed NEW BOILER SYSTEMS
1 - POST COMBUSTION
$ 24500 (SCR)
2 - MASSIVE FGR
  $ 3676
3 - POROUS MATRIX
$ 2787
4 - ULTRA LOW NOX TECHNOLOGY
$258

## Slide 127
Emission | Existing | Proposed
NOx ppm@3% O2 | 25.3 | 5 - 6
CO ppm@ 3% O2 | 70.2 | <50
Stack O2, % | 6.2 | 2.5 – 3.2
Reduce NOx by 75%
Reduce O2 by 48 - 60%
Reducing O2 from 6% to 3% saves this customer 273 CFH of nat gas
Existing Emissions & Goals

## Slide 128
Selective Catalytic Reduction (SCR)

## Slide 129: Selective Catalytic Reduction (SCR)
NOx control thru ammonia (NH3) injection
4NO + 4NH3 + O2  4N2 + 6H2O
2NO2 + 4NH3 + O2  3N2 + 6H2O
90-95% control
Problems
  Expensive
  High maintenance
  Ammonia “slip”
  Catalyst replacement
  & disposal

## Slide 130
Small Boiler with SCR

## Slide 131
Boiler with Retrofit SCR

## Slide 132
Ammonia Storage Tank

## Slide 133
Anhydrous Ammonia Storage Tank

## Slide 134
Utility Boiler NH3 Manifold

## Slide 135
NH3 Injection Tube

## Slide 136
SCR Catalyst

## Slide 137
% NOx Removed vs. Vanadium Pentoxide Catalyst Temperature

## Slide 138
Boilers
& SNCR

## Slide 139
Boiler With SNCR

## Slide 140
NOx control through ammonia or urea injection
No catalyst necessary
Temperature range 1400 oF – 1700 oF
Injected upstream of convection section
80% control under normal conditions
Problems:
  Changing flue temperatures with changing load
  Formation of ammonium salts
  Ammonia slip
Catalyst
Selective Non-Catalytic Reduction

## Slide 141
Technology | Approx. Reduction | Approx. lbs/MMBTU | Approx. ppmv @ 3% O2
Standard burners | Base case | 0.14 | 120
Low NOx burners | 60% | 0.06 | 45
Ultra Low NOx burners – Ist gen. | 80% | 0.03 | 25 - 30
Ultra Low NOx burners – 2nd gen. | 95% | 0.007 | 6 - 9
FGR | 55% | 0.025 | 20
Compu- NOx w/ FGR | 90% | 0.015 | 15 - 20
SNCR | 80% | 0.033 - 0.085 | 27 - 70
Catalytic Scrubbing | 70% | 0.017 - 0.044 | 14 - 36
SCR | 90 – 95% | 0.006 - 0.015 | 5 - 12
Comparison of NOx Reduction Technologies

## Slide 142
SOx Control

## Slide 143
Sulfur Content of Various Fuels
Fuel
Sulfur
Percent by Weight
Natural gas
0.0005
LPG
0.001
Fuel Oil No. 1
0.01 to 0.3
Fuel Oil No. 2
0.05 to 0.5
Diesel Motor Fuel
0.0015
Fuel Oil No. 4
0.2 to 1.75
Fuel Oil No. 5
0.5 to 1.75
Fuel Oil No. 6
0.5 to 1.75
Low Sulfur
Fuel Oil No. 6
0.5
Subbituminous coal
from Rocky Mt. states
0.3 to 1
Petroleum coke
2 to 10
Fuel Sulfur Content
Notes: TQ
#15

## Slide 144
Spray Tower Wet FGD Scrubber

## Slide 145
Five FGD Scrubber Modules on Utility Boiler

## Slide 146
PM Control

## Slide 147
Settling chambers
Cyclones
Baghouses
ESPs
Scrubbers
Control of Particulate Emissions

## Slide 148
Water Spray

## Slide 149
Soot Blowing

## Slide 150
Soot Blowers

## Slide 151
Soot Blowing/ Rapping

## Slide 152
Cyclone

## Slide 153
Multi-Cyclone

## Slide 154
Baghouse

## Slide 155
Baghouse
Clean
Dirty

## Slide 156
Electrostatic Precipitator (ESP)

## Slide 157
Regulatory
Requirements

## Slide 158: Regulatory Requirements
Federal, state, and local requirements
Boiler specific limits
Permit requirements
Monitoring requirements
Visible emission limits
Nuisance regulations
Breakdowns & variances

## Slide 159: Boiler Regulations
NSPS 40 CFR Part 60 Subpart D, Da, Db, Dc, Ea
Acid Rain Provisions (Parts 72,73,74,75, 76, 77, 78)
RCRA 40 CFR Parts 264 & 266
State Regulations including VE
SIP Requirements
Local Regulations
MACTs – JJJJJJ & DDDDD
Notes: USEPA regulations place limits on boiler emissions in NSPS & NESHAPS & ACID RAIN regulations.
Title 40 Part 60 Subparts D, Da, Db, and Dc of the CFR place emission limits on some steam generation units built since 1971.
Title 40 Part 63 Subparts JJJJJJ & DDDDD place emission limits toxic air contaminants
PM as surrogate for Heavy Metals
Hg
HCl as surrogate for inorganic HAPs
CO as surrogate for organic HAPS
based primarily on size, design and fuels used in boilers.

## Slide 160: Boiler Emission Limits
NOx, SO2, particulate, and opacity values for boilers are based on applicable subpart, heat input, date built or modified, and fuel used
States and districts may have more stringent limits

## Slide 161: Permit Categories
Emissions Limitations
Equipment Requirements
Operating Conditions
Monitoring and Recording Requirements
Compliance Testing
General Requirements

## Slide 162: Testing and Monitoring
Continuous Monitoring System
Stack Testing
Process Monitors
Recordkeeping

## Slide 163: Continuous Monitoring Types
Opacity Transmissometers
NOX
SO2
CO
O2 and/or CO2
Ammonia
Mercury Semi-Continuous

## Slide 164: Source Testing
Particulate Matter (PM, PM10, PM2.5)
NOx, SO2, CO, Ammonia
Mercury and Other Metals
Hydrogen Chloride
Formaldehyde
Visible Emissions (Method 9)

## Slide 165: Control Device Parameters
ESP Spark Rate and Fields in service
Baghouse Pressure Drop
Scrubber Pressure Drop and Liquor Flow Rate
Fuel Usage

## Slide 166: Alternative Monitoring
Portable analyzer monitoring of NOx, CO, O2
Determination of FGR rate
Burner mechanical adjustments
O2 Trim concentration
FGR valve(s) setting
Portable Combustion Analyzer

## Slide 167
Boiler Inspections

## Slide 168
Points of
Inspection
Capture
Transport
Air mover
Control device
Instrumentation
Subsystem
Records

## Slide 169
Prepare inspection form
File review
Regulation review
Equipment check
Pre-entry & entry
Pre-inspection meeting
Permit check
Pre-Inspection

## Slide 170: Reasons for Inspections
Compliance determination
Complaint investigation
Source plan approval
Review or renewal of permits
Special studies
AQMD

## Slide 171
Visible emission evaluation
General upkeep & maintenance
Monitoring instruments & records
Fuel type and quality
Maintenance records
Operational records
Source tests
Inspection

## Slide 172
Plant Safety

## Slide 173
Proper equipment
Plant warnings
Heat
High pressure steam
Electrical hazards
Noise
Moving parts
Inhalation hazards
Hazardous materials
Machine disintegration
Fires
Other hazards & traps
Inspector Safety
Notes: TQ
#24

## Slide 174
Plant Safety

## Slide 175
Plant Hazards

## Slide 176
Confined Space

## Slide 177
Confined Space

## Slide 179
HP Gas Lines

## Slide 180
Ruptured
Steam Line

## Slide 181
Steam Exhaust

## Slide 182
Access

## Slide 183
Access

## Slide 184
Questions?