## Slide 1
NACT 273
Industrial Boilers
Notes: First slide for 35mm show.

## Slide 2: Course Overview
Air Pollution
Boiler Uses
Boiler Theory and Operation
Air Pollution Formation
Air Pollution Control Devices
Boiler Regulations
Typical Permit Conditions
Inspection Procedures
Why
What
How
Notes: Ted

## Slide 3: Uses of Boilers
Electrical generation
Space heating
Food preparation
Commercial laundries
Pulp & paper industry
Petroleum industry
Chemical industry
Municipalities : Water, Sewage & Garbage
High Pressure (2,000 -3,800 psi)
Low Pressure (150 – 1,600 psi)
Liquid water
Liquid water and steam
Saturated Steam
Superheated Steam

## Slide 4: Small Firetube Boiler

## Slide 5
Industrial Boiler

## Slide 6: Babcock & Wilcox Utility Boiler

## Slide 7
CO Catalyst
SCR Catalyst
HP Steam Drum
HP Boiler #1
HP Boiler #2
LP Boiler
Deaerator
LP Steam Drum / DA Storage
HRSG
Boiler
Notes: Deaetrator storage

## Slide 8
Boilers &
Opacity

## Slide 9
History of Boilers : Ringelmann Chart

## Slide 10: Hot Numbers
British Thermal Unit (BTU)
  1 BTU the amount of energy needed to heat one pound of water one degree Fahrenheit or  energy given off by burning one wooden match
Lower Heating Value (LHV)
  Heating value of a fuel not counting
  heat needed to vaporize water
Higher Heating Value (HHV)
  Heating value of a fuel including heat needed to vaporize water

## Slide 11
Millions of BTU/hr
Boiler HP
Pounds of Steam/hr
Megawatts
Tons per day
Boiler Ratings

## Slide 12
Typical Boiler Rating

## Slide 13: Boiler Fuels
Natural gas
Diesel fuel oils
Tire Derived Fuel (TDF)
Coal/Petroleum Coke
Municipal waste
Bio-Mass
Waste gas
Nuclear

## Slide 14: Steam Plant Basic Elements

## Slide 15: Heat Transfer Methods
Notes: Radiant
Section

## Slide 16
Let’s Discuss Firetube &
Watertube Boilers
Notes: Ted?

## Slide 17: Fire-Tube Boiler

## Slide 18: Fire-Tube Boiler

## Slide 19: Small Fire-Tube Boiler

## Slide 20
Fire-Tube Boiler

## Slide 21: Water-Tube Boiler

## Slide 22
Water-Tube Boiler

## Slide 23: Boiler Construction
Graphics Courtesy of ERI
Notes: The section of the boiler, where the primary method of heat transfer from the flame to the tubes is radiation :
is often called the furnace, firebox, or radiant section of the boiler
10,000 – 15,000 pph

## Slide 24
Notes: Fire tube boilers and water tube boilers differ in how heat is transferred to generate steam.
In fire tube boilers, hot gases pass through tubes surrounded by water, while in water tube boilers, water flows through tubes surrounded by combustion gases.
Fire tube boilers are generally simpler and less expensive, suitable for smaller applications, while water tube boilers are more efficient and suitable for larger, high-pressure applications

## Slide 25
Boiler Tubes

## Slide 26
Boiler Tubes with Fins

## Slide 27
Boiler
Circulation

## Slide 28: Water to Steam Circulation Loop

## Slide 29
Boilers

## Slide 30
Natural
Circulation

## Slide 31
TEG Flow
Forced
Circulation

## Slide 32
Let’s Discuss Boiler
Air Requirements

## Slide 33: Boiler Air Requirements
Draft
  Natural
  Forced
  Induced
Combustion air
  Primary
  Secondary
  Excess

## Slide 34
Forced Draft Fans

## Slide 35
Induced Draft Fan
Notes: Forced draft fans push air into a system, creating positive pressure, while induced draft fans pull air out of a system, creating negative pressure.
Forced draft fans are often used for combustion air, while induced draft fans are used to draw out flue gases.

## Slide 36
Induced Draft Fans

## Slide 37: Gas Fired Water Tube Boiler

## Slide 38
Let’s Discuss Economizers
& Air-Preheaters

## Slide 39
Economizer – H2O Inside Tubes

## Slide 40
Air Pre-Heater

## Slide 41
Air Pre-Heater : Ambient to 400F +

## Slide 42
Fire Wall

## Slide 43
Refractory Lining
Boiler Tubes

## Slide 44
Boiler Tubes

## Slide 45
Let’s Discuss Fluidized
Bed Boilers

## Slide 46: Fluidized Bed Modes
Fixed
Bed
Minimum
Fluidization
Bubbling
Bed
Circulating
Bed
Start
No Air Flow

## Slide 47
Circulating Fluidized Bed (CFB)
Notes: Deseret CFB for waste coal project
A circulating fluidized bed (CFB) boiler is a type of boiler that uses fluidized bed combustion technology with a recirculating loop to improve combustion efficiency and reduce emissions. This technology allows for a
wide range of fuel types, including biomass, refuse-derived fuel, and even conventional fuels like coal and lignite. CFB boilers are particularly effective at capturing and recycling combustion byproducts like ash and
limestone

## Slide 48
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 49
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater
1
2
3
4
5
6
7
8
9
10

## Slide 50: Fluidized Bed Distributor Plate & Bubble Caps
Graphic Courtesy of B&W

## Slide 51
Enclosed Conveyors
Feed Lot

## Slide 52
Fuel Storage Silo
Enclosed Conveyor

## Slide 53
Water to Steam Loop

## Slide 54
Furnace
Economizer
Air Preheater
Superheater

## Slide 55
Pulverized
Coal Lines:
Gravity Fed

## Slide 56
Inside the
Boiler

## Slide 57
Water Tubes

## Slide 58
Water
Tubes

## Slide 59
Re-cir.
Fines
Nozzle
????

## Slide 60
Distributor Plates & Bubble Caps

## Slide 61
Bubble
Caps

## Slide 62
Bed Nozzles & Underfire Air

## Slide 63
Ash
Loadout

## Slide 64
High Pressure Steam Drums

## Slide 65
Steam Drum w/Cyclone & Chevron Separators

## Slide 66: STEAM DRUM INTERNALS CYCLONES WITH MESH PAD
STEAM OUTLET
CONTINUOUS BLOWDOWN
FEEDWATER INLET
CHEMICAL FEED
FEEDERS
RISERS
VORTEX BREAKER
MESH PAD

## Slide 67: STEAM DRUM INTERNALS BAFFLE PLATE WITH MESH PAD
STEAM OUTLET
MESH PAD
RISER
BAFFLE
FEEDER
RISER
CONTINUOUS BLOWDOWN
CHEMICAL FEED

## Slide 68
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater

## Slide 69
Circulating Fluidized
Bed Boiler
Interactive Exercise
Steam Drum
Primary Air
Secondary Air
Economizer
Startup Burner
Forced Draft Fan
Superheater
Multi-cyclone
Furnace
Air Heater
1
2
3
4
5
6
7
8
9
10

## Slide 70
Let’s Discuss
Power
Generation

## Slide 71
High Pressure Steam Lines

## Slide 72
High Pressure
Steam Lines

## Slide 73
Steam
Turbine

## Slide 74
Steam
Turbine

## Slide 75
Steam Turbine
Generator

## Slide 76
Cooling Towers

## Slide 77
Cooling Tower Shell

## Slide 78
Typical Control Room

## Slide 79
Utility Boiler
Steam
Turbine

## Slide 80
Steam
Turbine
Blades

## Slide 81
Steam Turbine

## Slide 82
HP Steam
Turbine

## Slide 83
Steam Turbine
Generator

## Slide 84: Brush DAX Turbogenerator

## Slide 85
Generator Rotor

## Slide 86
Generator Rotor

## Slide 87
Generator
Stator

## Slide 88
Step-Up Transformers

## Slide 89: Typical Electric Utility Plant
Boiler
Steam turbine
Generator
Cooling Media
Condenser
Deaerator
Stack
ESP
Induced Draft Fan
Forced Draft Fan
HP Feedwater Heaters
LP Feedwater Heaters
Fuel
Pump

## Slide 90
Let’s Discuss
Emissions
& Controls
Notes: Carl?

## Slide 91: Emissions From Boilers
Fuel
+
Air
(N2, O2)
H2O
CO2
CO
NOX
HC
SOX
PM
CHO
Notes: Recap from BASC107
Nox = NO and NO2
CHO = aldehydes such as formaldehyde

## Slide 92
NO2
NO
O
O2

## Slide 93: Emissions Control Methods
Boiler design
Proper maintenance
Operating conditions
Fuel types
Combustion
modifications
Exhaust treatment
Notes: Boiler design: Cir Fluidized Bed and FGR are boiler types that can reduce emissions of Nox (lower temps) and So2 (CFB limestone bed}
Proper main: like your car
Op cond: Lower temps
Fuel types: No or low sulfur fuel
Comb mods: Low Nox burners, OFA/SOFA
Add on controls – Baghouses, SCRs, SDAs

## Slide 94: Control of Gaseous Emissions
Low-NOx burners
OFA
Ammonia injection (SNCR)
Catalysts (SCR)
FGR
FGD
Notes: Lo NOx and ultra Lo NOx
OFA (Over-Fire Air) and SOFA (Separated Over-Fire Air) are combustion techniques used to reduce NOx (Nitrogen Oxides) emissions in industrial boilers. OFA and SOFA work by adjusting the air flow and fuel/air ratio within the combustion chamber to inhibit the formation of NOx. SOFA, a type of OFA, is designed to introduce air through a separate windbox above the burners, creating a fuel-rich zone below and a lean zone above to control NOx formation
SNCR and SCR fact sheets (per BASC107)
Flue gas recirculation (FGR) in boilers is a technique that lowers NOx emissions by recirculating a portion of the combustion gases back into the combustion chamber. This process reduces the peak flame temperature and the amount of oxygen in the combustion zone, thereby reducing the formation of thermal NOx. FGR can be implemented through internal recirculation, where gases are recirculated within the burner head, or external recirculation, where gases are recirculated from the flue and mixed with combustion air
FGD = wet scrubber, SDA, DSI (per BASC107)
Show EPA Control Cost manual section 5
https://www.epa.gov/economic-and-cost-analysis-air-pollution-regulations/cost-reports-and-guidance-air-pollution
EPA FGD Handout

## Slide 95: Combustion Considerations
Time
Temperature
Turbulence
Oxygen
Nitrogen
Notes: 3 Ts + O2
Too high a temp, more Nox
Too low temp or too much fuel, more CO

## Slide 96
 Thermal NOx
 Fuel-bound NOx
 Prompt NOx
NOx Creation
Notes: Thermal Nox most important
Then fuel bound
Prompt Nox least [slide to follow]
Prompt NOx - Prompt NOx is formed from molecular nitrogen in the air combining with fuel
in fuel-rich conditions which exist, to some extent, in all combustion. This nitrogen then oxidizes
along with the fuel and becomes NOx during combustion, just like fuel NOx. The abundance of
prompt NOx is disputed by the various writers of articles and reports - probably because they
each are either considering fuels intrinsically containing very large or very small amounts of
nitrogen, or are considering burners that are intended to either have or not have fuel-rich regions
in the flame.

## Slide 97: Thermal NOx vs. Temperature
Graphic Courtesy of Coen

## Slide 98: COMBUSTION MODIFICATION
NOx FORMATION
  N + O NO
  N + OH NO + H
NOx REDUCTION
  CH + NO HCN + O2 (Reversible)
  CH2 + NO HCN + OH (Reversible)
  C + NO CN + O2
  NHi + NO N2 + H2O
  THESE NOx REDUCTANTS ARE FORMED BY PARTIAL COMBUSTION IN A REDUCING ATMOSPHERE
  THE INTERMEDIATE SPECIES, HCN & CN, ARE CONVERTED TO N2, CO2 & H2O IN THE FINAL BURNOUT ZONE
Notes: OH = hydroxyl radical
NO = nitric oxide
CH = methylidyne
CH2 = methylene
HCN = hydrogen cynanide
Reduce NO (get rid of the O) and Oxidize CO (add an O)

## Slide 99: PROMPT NOx
Rapid Formation <1ms.
Little affect from temperature.
Presence of CHi & HCN during initial combustion can contribute to prompt NOx formation in an oxidizing environment, but will inhibit NOx formation in a reducing environment.
Presence of C & NHi in initial combustion process reduces the formation of prompt NOx.
Notes: The Prompt NOx mechanism describes the formation of NOx (Nitrogen Oxides) during combustion through reactions between atmospheric nitrogen (N2) and hydrocarbon radicals. This mechanism is generally less significant than Fuel NOx or Thermal NOx, but it becomes more important as NOx emissions are reduced
Not sure what last bullet is saying
DELETE Reactor combustion is controlled to a stoichiometry <.6 and a temperature <2400F.

## Slide 100: PROMPT NOx
N2
HCN
+C
CN
NO
+O
NCO
NHi
+CH2
+H
+OH
+H20
HNCO
+NO
+CH3
H2CN
+NHi
NO2
O2, H2O
HOCN
H

## Slide 101: NOx Production vs. Air/Fuel Ratio
Graphic Courtesy of Coen
Notes: Lean results in lower flame temps
Why NG engines are designed now to be lean burn
a lean burn engine uses a fuel-to-air ratio where there's more air than fuel, while a rich burn engine has more fuel than air. Lean burn engines generally offer better fuel economy and lower emissions, while rich burn engines can produce higher power and torque
Air is a lot cheaper than fuel (with no VOCs) = lean burn

## Slide 102: Industry Burner Definitions
Modern conventional burners
  NOx less than 80 ppm (<0.1 lb/MMBtu)
Low-NOx burners
  NOx less than 30 ppm
  (<0.04 lb/MMBtu)
Ultra Low-NOx burners
  9 ppm NOx
  (<0.01 lb/MMBtu)
Notes: These emission rates are for natural gas burners
The general nitrogen oxide emissions of low NOx burners are around 30-60 ppm. Nitrogen oxide emissions below 30ppm are usually called ultra low NOx burners to meet more stringent environmental protection requirements.
Boiler NSPS Nox limits (Da, Db, Dc):
Empire Generating Comb turbines = 42ppm (other than NG) or 15ppm (NG) at 15% 02 per NSPS KKKK [turbine NSPS]
Ultra low NOx burners can achieve NOx emission levels of 0.15 lb/MMBtu or lower when used in coal-fired power plants.
As compared to when SCR is added. 05 to .07 lb/MMBTU will be the limit 30 day rolling

## Slide 103
Let’s Discuss FGR
Notes: Carl

## Slide 104: Flue Gas Recirculation (FGR)
Notes: Flue gas recirculation (FGR) in boilers is a technique that lowers NOx emissions by recirculating a portion of the combustion gases back into the combustion chamber. This process reduces the peak flame temperature
and the amount of oxygen in the combustion zone, thereby reducing the formation of thermal NOx. FGR can be implemented through internal recirculation, where gases are recirculated within the burner head, or
external recirculation (as here), where gases are recirculated from the flue and mixed with combustion air
Up to 50% NOx reduction

## Slide 105: Flue Gas Recirculation (FGR)
Notes: See arrows

## Slide 106: Flue Gas Recirculation (FGR)

## Slide 107
FGR : Flue Gas
Recirculation
Notes: Carl

## Slide 108: FGR BURNERS
FEATURES
CAN USE FGR FLOWS AS HIGH AS 40% OF THE TOTAL STACK EFFLUENT
SOME SYSTEMS OPERATE VERY CLOSE TO THE LIMITS OF FLAMABILITY
SOME SYSTEMS OPERATE WITH VERY RAPID MIXING, VERY CLOSE TO STOICHIOMETERY.
CON’S
HIGH ELECTRICAL USAGE (FGR fan HP doubled compared to RX system)
LOW TEMPERATURE, TRANSLUCENT, FLAME REDUCES HEAT TRANSFER & EFFICIENCY.
COMBUSTION INSTABILITY
CAN’T CHANGE FIRING RATE FAST ENOUGH TO FOLLOW CHANGING LOAD DEMANDS

## Slide 109: Lower Cost to Industry
Simple durable refractory and steel construction results in:
  Lower initial cost
  Lower maintenance costs
Lower operating cost
  Less stack losses due to low excess air and low FGR requirements
  Lower fan costs
  Eliminates the need for chemicals & catalysts

## Slide 110: Flame Temperature vs. FGR
Graphic Courtesy of Coen

## Slide 111: FGR Impact
Notes: Around 50%

## Slide 112
Let’s Discuss
Staged Combustion

## Slide 113: Gas Pre-mix Burner
Notes: Graphic of a burner
Burner in which part, or all, of the air for complete combustion of the gas, is mixed with the gas upstream of the mixture outlet ports. For example, air and gas are thoroughly mixed before the burner head in premixed burners.

## Slide 114: Low-NOx Burner with Staged Fuel
Notes: Staged Fuel and Air: Instead of mixing fuel and air completely before combustion, a low-NOx burner with staged fuel and air introduces them in stages.
Designed to reduce NOx emissions by controlling the combustion process through staged fuel and air injection. This technique involves introducing fuel and air in different stages within the combustion chamber, promoting better mixing and reducing peak flame temperatures, which in turn minimizes the formation of NOx

## Slide 115: Low-NOx Burner with Staged Fuel
Notes: TQ
#12
TQ
#11

## Slide 116
Ultra Low-NOx Burner (9 ppm)
Notes: 9ppm = .01 lbMMBTU

## Slide 117
Notes: 16 mixers around circumference

## Slide 118
Notes: Pretty complicated manifolding

## Slide 119: Burner Cross-sectional View

## Slide 120: TYPICAL COMPONENTS
Fuel valves & Servos
Lean Jet
Reactor

## Slide 121: TYPICAL COMPONENTS
REACTOR PORT
LEAN JETS

## Slide 122: A Look Down the Furnace
Rich Flame
Lean Flames (x4)
Burnout Zone
FGR

## Slide 123: Staged Combustion with Overfire Air
Notes: OFA

## Slide 124: Burners with Overfire Air
Graphic Courtesy of B&W
Notes: Inside furnace

## Slide 125: NOx Reduction by Boiler Configuration
A B C
A: Low-NOx burner only, no overfire air (OFA)
B: Low-NOx burner with OFA
C: Low-NOx burner with OFA and FGR
Graphic Courtesy of B&W
Notes: Gas fired

## Slide 126: COST $/ TON NOx REMOVED NEW BOILER SYSTEMS
POST COMBUSTION
$ 24500 (SCR)
MASSIVE FGR
  $ 3676
POROUS MATRIX
$ 2787
ULTRA LOW NOX TECHNOLOGY
$258
Notes: Don’t think we mentioned Porous Matrix burners (PMBs) before, which utilize porous materials like ceramics, promote better fuel-air mixing and can control the flame zone temperature to reduce NOx formation.
Not sure what “massive” FGR is.

## Slide 127: Existing Emissions & Goals
Emission | Existing | Proposed
NOx ppm@3% O2 | 25.3 | 5 - 6
CO ppm@ 3% O2 | 70.2 | <50
Stack O2, % | 6.2 | 2.5 – 3.2
Reduce NOx by 75%
Reduce O2 by 48 - 60%
Reducing O2 from 6% to 3% saves this customer 273 CFH of nat gas
Notes: Reduce excess air (i.e, O2) thru FGR or low Nox burners – use less fuel and reduce Nox and CO
Sounds straightforward but needs to be highly engineered and designed.

## Slide 128
Let’s Discuss
SCR
Catalyst
Notes: Carl?

## Slide 129: Selective Catalytic Reduction (SCR)
NOx control thru ammonia (NH3) injection
4NO + 4NH3 + O2  4N2 + 6H2O
2NO2 + 4NH3 + O2  3N2 + 6H2O
90-95% control
Problems
  Expensive
  High maintenance
  Ammonia “slip”
  Catalyst replacement & disposal
Notes: All the things we talked about in BASC107

## Slide 130
Small Boiler with SCR

## Slide 131: Boiler with Retrofit SCR
Notes: Recall SCR system is typically located downstream of the economizer (for boiler water) and upstream of the air heater (for combustion air).

## Slide 132
Ammonia Storage Tank
Notes: NH3 in water

## Slide 133
Anhydrous Ammonia Storage Tank
Notes: Dry HN3
Pro and cons of anhy and aq NH3 and urea

## Slide 134
Utility Boiler NH3 Manifold

## Slide 135
NH3 Injection Tube

## Slide 136
SCR Catalyst
Notes: Honeycomb of plate

## Slide 137: % NOx Removed vs. Vanadium Pentoxide Catalyst Temperature
Notes: VnO cat is a base metal cat – run at 600 to 750F
Same pro/coms as listed in BASC107
In Selective Catalytic Reduction (SCR) systems, precious metals (like platinum, palladium, and rhodium) and base metal oxides (like vanadium, molybdenum, and tungsten) are both used as catalysts, each with its own advantages and disadvantages. Precious metals excel at low-temperature NOx reduction and high nitrogen selectivity, but can be costly and may be prone to poisoning. Base metal oxides are more abundant and cost-effective, offering a wider temperature window and often showing good NH3 oxidation ability.

## Slide 138
Boilers
& SNCR

## Slide 139: Boiler With SNCR
Notes: Here upstream of Economizer

## Slide 140: Selective Non-Catalytic Reduction
NOx control through ammonia or urea injection
No catalyst necessary
Temperature range 1400 oF – 1700 oF
Injected upstream of convection section
80% control under normal [optimal] conditions
Problems:
  Changing flue temperatures with changing load
  Formation of ammonium salts
  Ammonia slip
Catalyst
Notes: Note higher operating temp range vs SCR
80% seems optimistic, maybe in gas or coal fired boilers more like 40% - depends on baseline Nox levels.
Overall % if boiler and burner Nox controls are also being used.
Potentially achieving up to 80% NOx removal under optimal conditions

## Slide 141: Comparison of NOx Reduction Technologies
Technology | Approx. Reduction | Approx. lbs/MMBTU | Approx. ppmv @ 3% O2
Standard burners | Base case | 0.14 | 120
Low NOx burners | 60% | 0.06 | 45
Ultra Low NOx burners – Ist gen. | 80% | 0.03 | 25 - 30
Ultra Low NOx burners – 2nd gen. | 95% | 0.007 | 6 - 9
FGR | 55% | 0.025 | 20
Compu- NOx w/ FGR | 90% | 0.015 | 15 - 20
SNCR | 40% 80% | 0.033 - 0.085 | 27 - 70
Catalytic Scrubbing | 70% | 0.017 - 0.044 | 14 - 36
SCR | 90 – 95% | 0.006 - 0.015 | 5 - 12
Notes: See slide 66 in BASC107 course – SNCR was 40%
30 – 75% in EPA’s CCM depending on other NOX controls

## Slide 142
Let’s Discuss
SOx Control
Notes: Carl
Remember from NASC107: 3 types of add on control – wet scrubber, spray dryer absorber (SDA), dry sorbent injection (DSI)

## Slide 143: Fuel Sulfur Content
Sulfur Content of Various Fuels
Fuel
Sulfur
Percent by Weight
Natural gas
0.0005
LPG
0.001
Fuel Oil No. 1
0.01 to 0.3
Fuel Oil No. 2
0.05 to 0.5
Diesel Motor Fuel
0.0015
Fuel Oil No. 4
0.2 to 1.75
Fuel Oil No. 5
0.5 to 1.75
Fuel Oil No. 6
0.5 to 1.75
Low Sulfur
Fuel Oil No. 6
0.5
Subbituminous coal
from Rocky Mt. states
0.3 to 1
Petroleum coke
2 to 10
Notes: What's even easier? no Sulfur in the fuel.
Ultra low sulfur diesel and fuel oil now used – 15ppm .0015% [Empire Generating required to use this distillate oil in the generator]
Low sulfur diesel pre 2006 was 500ppm .05%
Liquified petroleum gas
TQ
#15

## Slide 144: Spray Tower Wet FGD Scrubber
Graphic Courtesy of B&W
Notes: Babcock and Wilcox

## Slide 145: Five FGD Scrubber Modules on Utility Boiler
Graphic Courtesy of B&W
Notes: Again from BASC107

## Slide 146
Let’s Discuss
PM Control

## Slide 147: Control of Particulate Emissions
Settling chambers
Cyclones
Baghouses
ESPs
Scrubbers
Notes: Settling chambers and cyclones = knock out box for very course PM (>PM10)
but multiclone can achieve 90% control of 5-10 micron particles.
Baghouses and scrubbers for fine PM10 and 2.5

## Slide 148
Water Spray
Notes: Fugitive PM control
Fugative dust control plan can sometimes be part of a permit

## Slide 149
Soot Blowing
Notes: To clean boiler tubes, restore heat transfer efficiency

## Slide 150
Soot Blowers

## Slide 151
Soot Blowing/ Rapping
Notes: Hopefully that is in compliance with the sources permit!

## Slide 152
Cyclone

## Slide 153: Multi-Cyclone
Graphic Courtesy of B&W

## Slide 154
Baghouse
Notes: Many bags per chamber. Exhaust air goes up the inside of bag

## Slide 155
Baghouse
Clean
Dirty

## Slide 156
ESP
Notes: Ted talked about

## Slide 157
Regulatory
Requirements
Notes: Will discuss in a few slides - Boiler NSPS Part 60: D, Da, Db, Dc
D [Steam EGUs]: >250MMBTU, after 1971, limits for SO2, NOx (expressed as NO2), PM
Da[Steam EGUs]: >250MMBTU after 1978, limits for SO2, NOx (expressed as NO2), PM
Db [industrial/commercial steam GUs]: >100MMBTU after 1984, limits for SO2, NOx (expressed as NO2), PM
Dc [small steam industrial/commercial steam GUs]: >10>100 MMBTU after 1989, limits for SO2 and PM
MACT Part 63 DDDDD – “5Ds” [industrial boilers and process heaters]: new as of 2013 table 1 (limits for HCl, Hg, CO. PM), existing table 2 (limits for HCl, Hg, CO. PM)
MACT JJJJJJ – “6 Js” [Industrial, Commercial, and Institutional Boilers Area Sources]: new as of 2010 table 1 (emission limits – PM, Hg, CO) table 2 (Work Practice Standards, Emission Reduction Measures, and Management Practices)

## Slide 158: Regulatory Requirements
Federal, state, and local requirements
Boiler specific limits
Permit requirements
Monitoring requirements
Visible emission limits
Nuisance regulations
Breakdowns & variances
Notes: NSPS and MACT rules, SIP requirements, state/local only regs
Permit limits under minor NSR, PSD, or state only permit
Nuisance = odor and noise, sometimes fugitive dust from area sources (not federally enforceable)
SSM = startup shutdown and malfunction provisions (in SIP and/or permits), a lot of those provisions in the Empire Gen TV permit

## Slide 159: Boiler Regulations
NSPS 40 CFR Part 60 Subpart D, Da, Db, Dc, Ea
Acid Rain Provisions (Parts 72,73,74,75, 76, 77, 78)
RCRA 40 CFR Parts 264 & 266
State Regulations including VE
SIP Requirements
Local Regulations
MACTs – JJJJJJ & DDDDD
MATs for EGUs
Notes: Boiler NSPS Part 60: D, Da, Db, Dc
D [Steam EGUs]: >250MMBTU, after 1971, limits for SO2, NOx (expressed as NO2), PM
Da[Steam EGUs]: >250MMBTU after 1978, limits for SO2, NOx (expressed as NO2), PM
Db [industrial/commercial steam GUs]: >100MMBTU after 1984, limits for SO2, NOx (expressed as NO2), PM
Dc [small steam industrial/commercial steam GUs]: >10>100 MMBTU after 1989, limits for SO2 and PM
MACT Part 63 DDDDD – “5 Ds” [industrial boilers and process heaters]: new as of 2013 table 1 (limits for HCl, Hg, CO. PM), existing table 2 (limits for HCl, Hg, CO. PM)
MACT JJJJJJ – “6 Js” [Industrial, Commercial, and Institutional Boilers Area Sources]: new as of 2010 table 1 (emission limits – PM, Hg, CO) table 2 (Work Practice Standards, Emission Reduction Measures, and Management Practices). See course handouts for more on boiler area source MACT rule.
Also for EGUs MACT UUUUU – controversial MATs rule [2012 and 2024 (now being reconsidered)]
Acid Rain program for large EGUs
RCRA 264/266 and MACT EEE: burning haz waste in a boiler, industrial furnace, or incin.
USEPA regulations place limits on boiler emissions in NSPS & NESHAPS & ACID RAIN regulations.
Title 40 Part 60 Subparts D, Da, Db, and Dc of the CFR place emission limits on some steam generation units built since 1971.
Title 40 Part 63 Subparts JJJJJJ & DDDDD place emission limits toxic air contaminants
PM as surrogate for Heavy Metals
Hg
HCl as surrogate for inorganic HAPs
CO as surrogate for organic HAPS
based primarily on size, design and fuels used in boilers.

## Slide 160: Boiler Emission Limits
NOx, SO2, particulate, and opacity values for boilers are based on applicable subpart, heat input, date built or modified, and fuel used
States and districts may have more stringent limits
Notes: Show tables in Part 60 and 63 (TSM = total selected metals)

## Slide 161
BACT in CA
Notes: Empire as a turbine is 15ppm per NSPS and BACT

## Slide 162
BARCT & RACT
Notes: Explain RACT

## Slide 163: Permit Categories
Emissions Limitations
Equipment Requirements
Operating Conditions
Monitoring and Recording Requirements
Compliance Testing
General Requirements
Notes: Show a boiler permit? Coal Strip?
Look at a TV permit Section II page 6, Section III.C page 22 and 23
Units 3 and 4 each have about 740 megawatts of generating capacity
Nox .18lb/MMBTU >400MW .30lb/MMBTU <400MW 30-day rolling
Subject to MATs Rule 63 UUUUU
Talk more about permitting in PERM202 course

## Slide 164: Testing and Monitoring
Continuous Monitoring System
Stack Testing
Process Monitors
Recordkeeping

## Slide 165: Continuous Monitoring Types
Opacity Transmissometers
NOX
SO2
CO
O2 and/or CO2
Ammonia
Mercury Semi-Continuous
Notes: Perf Spec in Part 60 Appx B (QA in Appx F)
PS1 Opacity, PS2 for Nox and SO2, PS4 for CO, PS3 for O2 and CO2, PS12 for Hg
NH3 FTIR PS15

## Slide 166: Source Testing
Particulate Matter (PM, PM10, PM2.5)
NOx, SO2, CO, Ammonia
Mercury and Other Metals
Hydrogen Chloride
Formaldehyde
Visible Emissions (Method 9)
Notes: Stack testing – Part 60 Appx A
PM: method 5 Nox: M7 SO2: M6 CO: M10 Metals: M29 Hg M30 HCl: M26
CH2O: M323 part 63 appx A
VE: M9 [on exam]
Check with agency stack testing staff

## Slide 167: Control Device Parameters
ESP Spark Rate and Fields in service
Baghouse Pressure Drop
Scrubber Pressure Drop and Liquor Flow Rate
Fuel Usage
Notes: Covered this in BASC107 These are indirect parameters in lieu of stack tests and CEMs. If they are within indicator ranges then good confidence emission limits are being met – ranges set during stack testing.
Baghouse – in addition to pressure drop, broken bag detectors (triboelectric sensors)
CAM is related to this

## Slide 168: Alternative Monitoring
Portable analyzer monitoring of NOx, CO, O2
Determination of FGR rate
Burner mechanical adjustments
O2 Trim concentration
FGR valve(s) setting
Portable Combustion Analyzer

## Slide 169
Boiler Inspections
NACT350 Basic Inspector
NACT355 Advanced Inspector
Notes: Air Knowledge instructor led courses on inspections, compliance and enforcement

## Slide 170
 Capture
 Transport
 Air mover
 Control device
 Instrumentation
 Subsystem
 Records
Points of
Inspection
Notes: Like we did at Empire Generating – walk the process flow diagram, combustion/exhaust gas, liquid flows, check instrumentation and gauges in situ

## Slide 171: Pre-Inspection
Prepare inspection form
File review
Regulation review
Equipment check
Pre-entry & entry
Pre-inspection meeting
Permit check
Notes: Prior to the site inspection the inspector should review all information available in the district source files including: approved permits, equipment lists, conditions for each permit, previous inspection reports, Notices of Violation, breakdown reports, enforcement actions taken, odor complaints, variance histories, alternative emissions control plans, abatement orders, source tests, and the design of the plant.
Verify that all applicable permits for the facility are current and valid. Bring a current copy of the permit(s) and bring extra copies in case the facility has misplaced or lost their copy.
The inspector may wish to complete some portions of the inspection documentation before arriving at the facility as this will save time during the pre-inspection meeting. If your district has checklists or rule specific forms, use them.
You should review any references to the specific rules which are noted in the source files. In particular, be familiar with each standard and exemption in the rules. Discuss regulations that apply to the facility with experienced personnel
d meeting last

## Slide 172: Reasons for Inspections
Compliance determination
Complaint investigation
Source plan approval
Review or renewal of permits
Special studies
AQMD
Notes: Examples of special studies would be operating and maintenance evaluations or updating emission inventories.

## Slide 173: Inspection
Visible emission evaluation
General upkeep & maintenance
Monitoring instruments & records
Fuel type and quality
Maintenance records
Operational records
Source tests
Notes: RATA = relative accuracy test audit.
Make sure that you have the proper safety equipment available for use during the inspection. When you arrive at the plant, notice if there are any visible emissions. If there are any visible emissions, make sure you document them and plan on finding the sources as soon as possible after entering the facility.
Request to see the previous contact mentioned in the files. Depending on the facility, it may be the environmental coordinator, supervisor, president, maintenance worker or operator. Always present your business credentials immediately to avoid confusion.
If the source is unfamiliar with your district’s authority be prepared to cite and provide copies of Right of Entry. Know and follow your district’s policy if the facility refuses entry.
Before the inspection begins the inspector should meet with the source representative to obtain operating information. The inspector should state the purpose of the inspection and identify the equipment which will be inspected. Facility information can be verified during this meeting including: the facility name and ownership, address complete with city and zip code, contact name, contact title, phone number and area code. Discuss safety procedures and whether or not there have been any problems in the past. Request a copy of applicable material safety data sheets (MSDS). If necessary discuss sampling procedures with the source representative.
Check existing permit conditions and ask if any other changes have been made to the operation which are not reflected in the permit.

## Slide 174
Plant
Safety

## Slide 175: Inspector Safety
Proper equipment
Plant warnings
Heat
High pressure steam
Electrical hazards
Noise
Moving parts
Inhalation hazards
Hazardous materials
Machine disintegration
Fires
Other hazards & traps
Notes: Safety video!
Let plant POC lead entry into any operating plant areas
Don’t touch anything in the plant – assume hot!
Use proper PPE regardless of what plant personnel do
TQ
#24

## Slide 176
Plant Safety
Notes: Slip trip and fall, heat, moving equipment, confined space (insufficient O2).

## Slide 177
Plant Hazards

## Slide 178
Confined
Space

## Slide 179
Confined
Space
Notes: Note signage: Confined space permit needed

## Slide 181
HP Gas Lines

## Slide 182
Ruptured
Steam Line

## Slide 183
Steam
Exhaust
Notes: HP steam is not like fog

## Slide 184
Access

## Slide 185
Access

## Slide 186
Thank You!